- SECTION 26 09 00

- ELECTRICAL THERMAL MONITORING

- GENERAL

  - SCOPE

    - This section defines the low voltage thermal solution for use in the AC electrical equipment as outlined in the one-line and/or riser drawings. These solutions will provide a low voltage thermal system integrated into the electrical equipment. The thermal system shall provide the ability to report thermal information remotely using a web-based software platform.

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

    - Related Sections include the following:

      - [Section 26 23 00  – Low Voltage Switchgear]

      - [Section 26 24 13 – Switchboard]

      - [Section 26 24 16 – Panelboards]

      - [Section 26 24 19 – Motor Control Centers]

      - [Section 26 xx xx – Electrical Installation]

  - SUBMITTALS

    - Submit shop drawings and product data for approval and final documentation in the quantities listed according to the Conditions of the Contract.  Customer name, customer location, and customer order number shall identify all transmittals.

    - [Final Documents: Record documentation to include but not limited to as-built wiring diagrams, thermal monitoring location schedule, factory test results and certificate(s), system commission report, manufacturers contact information, operation, and installation manuals.]

  - RELATED STANDARDS AND COMPLIANCE

    - Meet the following recognized standards and approvals for applications:

      - Accuracy:

- Range: 40°C to 105°C (± 2°C) / 104°F to 221°F (± 4°F)

      - Safety/Construction/EMC

        - CSA C22.2 No. 61010-1 Safety Requirements for Electrical Equipment for Measurement

        - UL 61010-1 (IEC 61010-1) Safety Requirements for Test & Measurement.

      - Electro Magnetic Compatibility

        - Compliant with UL 61010-1, CAN/CSA-C22.2 No. 61010-1, IEC 61010-1

        - Compliant with EMC standards IEC 61326-1, IEC 61326-2-3

        - Compliant with FCC CFR47 Part 15 Subpart B:2018 Class B

      - Security Standards

        - Compliant with IoT Security standard OWASP IoT Top 10-2018

      - Environmental Conditions

        - Altitude up to 3000 meters

        - Maximum relative humidity is 80% for temperatures up to 31°C, decreasing linearly to 50% relative humidity at 40°C

        - Pollution Degree 3

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: The Manufacturer of this equipment shall have a minimum of 5 years’ experience producing electronic system equipment.

    - Manufacturer shall provide both external and embedded thermal solutions.

    - Comply with requirements of latest revisions of applicable industry standards.

    - Manufacturer shall have local & remote software solutions.

    - Thermal monitoring hardware shall be designed, factory-installed, and dielectric voltage withstands test after the installation before shipping to site.

    - Embedded solution must be a standard product offering by the panel manufacturer.  Custom “one-off” installed thermal solutions are not acceptable.

  - DELIVERY, STORAGE AND HANDLING

    - Store and handle in strict compliance with manufacturer’s instructions and recommendations.  Protect from potential damage from weather and construction operations.  If the thermal monitoring parts are installed in equipment, store the equipment so condensation will not form on or in it.  If necessary, apply temporary heat where required to obtain suitable service conditions.

- PRODUCTS

  - MANUFACTURERS

    - The low voltage thermal monitoring shall be a SEM3T thermal solution by Siemens or pre-approved equal.  Approved manufacturers are as follows:

      - SIEMENS

      - [  ]

      - [  ]

  - HARDWARE OVERVIEW

    - Thermal Sensors – Manufacturer, shall offer different sizes of thermal sensors.

      - Thermal Sensors shall be pre-calibrated and will never need future calibration.

      - Thermal Sensors shall be rated for 600VAC.

      - Thermal Sensors standard wire length shall be 10 feet and shall be extended up to 50 feet

      - Thermal Sensors wire shall be UL rated operating temperature to 200 deg C, 600V rated, UL style 1199, 18AWG, 10 x 30 stranded

    - Thermal Modules – Individual micro thermal modules shall be provided, one for thermal monitoring locations. These thermal modules will tie to the thermal sensors.  The manufacturer of the thermal modules must supply the thermal sensors.

      - When grouped, the thermal Modules shall allow for measurement of each thermal measurement point.

      - The Thermal Module shall accept inputs from all available thermal sensors, both screw ring terminals and cylindrical sensor terminals.

      - Setup for each thermal Module shall be done through the Controller web page.

      - Thermal modules shall plug directly into the rack without any additional installation work or tools needed.

      - All embedded thermal solutions shall have the thermal modules installed at the electrical equipment manufactures factory. No field installation shall be required.

    - Racks – Thermal Modules are to be mounted on scalable Racks.  The Rack Assembly shall be designed to allow the Thermal Modules to be snapped into the Rack without using any tools.

      - Rack Assemblies shall be available in sizes of 3, 6, 9, 15, and 21 Thermal Modules.

      - Rack Assemblies shall be sized to all denoted thermal locations on the drawings accept up to 3, 6, 9, 15 or 21 Thermal Modules.

      - Rack Assemblies will allow for open slots to accommodate future expansion, as noted on the drawings.

      - Rack Assemblies shall be connected to the Controller using a 600v rated communications cable.

    - Controller – The controller shall function as the collection, processing, and setup location for the thermal modules/sensors with a built-in web page interface.

      - The Controller shall support up to 4 concurrent Modbus TCP connections including one of the connections that would be accessing the built-in webpages through standard browsers such as Chrome and Internet Explorer.

      - The Controller shall be synchronized with the NTP server for Date & Time.

      - Built-in Web page configuration and real-time data screens will include:

        - System settings: IP Configuration, SMTP email configuration, Measurement Units (Celsius or Fahrenheit), and System Time Setup.

        - Global settings: for threshold and set-point alarms.

        - Individual Thermal Module threshold and set-point alarm configurations

        - Real-time data monitoring for instantaneous thermal data, last minimum, and maximum with the timestamp.

        - Grouping of multiple thermal location logging and alarming

        - Real-time data logs, alarm event logs and system event logs for historical trending dashboard (Today, Yesterday, DTD, WTW, MTM, YTY comparisons), emailing, download in CSV format, and alarm notifications.

        - User Profile and User Configuration

        - Diagnostics pages allow users to download monitored Modbus register address information passed to other monitoring system or 3rd party control systems.

        - Firmware upgrade and webpage upgrade done through built-in web pages. No external software tool is required to upgrade the firmware on the hardware.

        - Thermal Module serial numbers and Controller serial number display.

        - Import and export of saved configurations in a file format.

        - Support of English, German, French, and Spanish languages on all built-In webpages.

        - No additional software shall be required to configure the Controller or Thermal modules.

      - The Controller shall communicate thermal values to external/third-party systems by:

        - HTML Web page interface, Modbus TCP.

      - One Controller shall be able to manage up to 45 Thermal Modules.

      - The Controller shall have a dual ethernet port for daisy-chaining controller over ethernet communications.

      - The Controller shall be powered from a 24vDC power supply source

    - Thermal Data – Data recorded and calculated that can be passed on to an external system or displayed on the Controllers web page shall include for thermal locations:

      - Instantaneous: The system shall provide for the following parameters.

        - Instantaneous Temperature

        - Temperature Rise

        - Minimum Temperature with Timestamp

        - Maximum Temperature with Timestamp

        - Mean Temperature

      - Alarming/Monitoring: The system shall display and configure alarming for the following parameters

        - Under Temperature Warning

        - Under Temperature Alarm

        - Over Temperature Warning

        - Over Temperature Alarm

    - Onboard Data Logging

      - System shall data log up to 1 year for selected data registers.

      - System shall allow a maximum of 16 data logs

      - System shall have a selectable option for logging the data at different interval times.

      - System shall have an option to down the Datalog file in .CSV format in one-click download

      - System shall have an option to data log by created groups.

    - Onboard Dashboards

      - System shall display the trending of various data points for individual thermal points

      - System shall have a maximum of 4 data points to display in trending graphs.

      - System shall have an option to select historical trending by Today, Yesterday, Day to Day, Week to Week, Month to Month, and Year to Year comparison.

      - System shall have an onboard default dashboard that is fed from automatic data logging and compression, not from customer-defined data logging.

    - Grouping

      - System shall have an option to data logs by created groups.

      - System shall display trending of various grouped data points

    - Emailing

      - System shall have an option to configure sending the log files and alarm notifications via valid email address and schedule notification

- EXECUTION

  - INSTALLATION

    - The Contractor shall furnish, install and terminate all communication conductors and associated conduits external to any factory supplied equipment.

    - All communications conductor wiring and routing shall be per the manufacturer's recommendations and as shown on the contract drawings.

    - Additional connections to thermal systems, where applicable, shall be done in the field by [the manufacturer’s start-up service group][the installing contractor].

  - ADJUSTING AND CLEANING

    - The thermal sensors shall be pre-calibrated and require only basic setup via the embedded web pages.

    - Clean exposed surfaces using manufacturer recommended materials and methods.

  - TESTING

    - Perform factory and installation tests in accordance with applicable NEC, NEMA, UL, IEC.

  - WARRANTY

    - Equipment manufacturer warrants that all goods supplied are free of non-conformities in quality and materials for one year from the date of initial operation, but not more than eighteen months from the date of shipment.

  - STARTUP SERVICES

    - Engage a factory-authorized service representative to perform startup service of the thermal monitoring system.  The representative shall be trained and qualified for thermal monitoring systems.

    - Provide a qualified tradesperson to assist in the commissioning of the system.

    - Obtain and submit as part of final documents a field commissioning report.

    - Verify that the [thermal point is] [thermal points are] installed and connected according to the Contract Documents.

    - Complete installation and startup check according to manufacturer's written instructions.

  - SUPPORT

    - The electrical equipment manufacturer shall provide a 1-800 number for telephone support.

    - The vendor shall provide training at a dedicated training facility, complete with software, devices, and demonstrations, or offer remote training services if required.

    - The vendor shall also provide online support for technical information and literature.

END OF SECTION