## PGE System Data
PGE Interconnection Data |  | DISCLAIMER: This distribution system information provides a high-level system overview and is provided for information purposes only. It is not intended to replace the established interconnection process. This information represents a snapshot of the system and the interconnection queue at the time it was produced, is not updated with every system or queue change, and may not reflect the current system or queue. Project-specific interconnection requirements and costs can be determined only by completing the applicable interconnection process. To obtain the right to interconnect to PGE’s system, a project must complete the applicable interconnection process. PGE shall not be held liable under any circumstances for any errors, omissions, inaccurate, and/or out-of-date content or information provided. By producing this distribution system information, PGE makes no warranty or guarantee about the ability to interconnect or costs to do so. In addition, PGE makes no warranty of merchantability or fitness for any particular purpose and disclaims any and all liability with respect to the accuracy or currency of the information provided, or the fitness or appropriateness of the information for any particular use. This information is supplied with all faults.
Substation Name | Substation Location | Feeder Name | Feeder ID# | Feeder Voltage (kV) | County | SCADA (Y/N) | Transformer position | Transformer rating (MVA) | Feeder Peak Load (MVA) | Feeder Net Daytime Minimum Load (MW) | Distribution line rating (MVA) [Note: The conductor is the first feeder section outside the substation. This is not necessarily the smallest conductor in the entire backbone of the feeder.] | DG Capacity Connected (MW) [includes small gen & net metering] | DG Capacity In Queue (MW) [includes small gen only] | Generation Limited (Y/N) | Gen Nameplate: Min Consumption Ratio GEN/(GEN + Net DML) | Future DML (MW) (Net DML - DG Capacity in Queue) | Future Gen Nameplate: Min Consumption Ratio (feeder) | Feeder Equipped for DG Readiness | Transformer Equipped "DG Ready" with Configuration or 3V0 Protection
ABERNETHY | Oregon City | ABERNETHY-CLACKAMAS HEIGHTS | 6105013 | 13 | CLACKAMAS | Y | ABERNETHY WR2 | 28 | 5.8 | 1.7407 | 14.3 | 0.02529 | 0 | N | 1.432% | 1.7407 | 1.432% | N | N
ABERNETHY | Oregon City | ABERNETHY-OREGON CITY | 6105023 | 13 | CLACKAMAS | Y | ABERNETHY WR1 | 16.8 | 8.8 | 2.8581 | 17.8 | 0.68853 | 0 | N | 19.41% | 2.8581 | 19.41% | N | N
ABERNETHY | Oregon City | ABERNETHY-TRANSIT | 6105033 | 13 | CLACKAMAS | Y | ABERNETHY WR1 | 16.8 | 5.2 | 1.9085 | 17.8 | 0.15934 | 0 | N | 7.705% | 1.9085 | 7.705% | N | N
ABERNETHY | Oregon City | ABERNETHY-WASHINGTON | 6105043 | 13 | CLACKAMAS | Y | ABERNETHY WR2 | 28 | 6.9 | 2.9702 | 17.8 | 0.24243 | 0 | N | 7.546% | 2.9702 | 7.546% | N | N
ALDER | Portland | ALDER-ANKENY | 1118013 | 13 | MULTNOMAH | Y | ALDER WR1 | 28 | 6.5 | 2.5318 | 17.8 | 0.13922 | 0 | N | 5.212% | 2.5318 | 5.212% | N | N
ALDER | Portland | ALDER-IRVING | 1118053 | 13 | MULTNOMAH | Y | ALDER WR2 | 28 | 9.2 | 3.5663 | 18.4 | 0.24853 | 0 | N | 6.515% | 3.5663 | 6.515% | N | N
ALDER | Portland | ALDER-LINCOLN | 1118043 | 13 | MULTNOMAH | Y | ALDER WR1 | 28 | 4.4 | 1.6277 | 17.8 | 0.17788 | 0 | N | 9.852% | 1.6277 | 9.852% | N | N
ALDER | Portland | ALDER-STARK | 1118033 | 13 | MULTNOMAH | Y | ALDER WR1 | 28 | 10.7 | 4.5337 | 18.4 | 0.08066 | 0 | N | 1.748% | 4.5337 | 1.748% | N | N
ALDER | Portland | ALDER-TAYLOR | 1118063 | 13 | MULTNOMAH | Y | ALDER WR2 | 28 | 10.9 | 3.935 | 17.8 | 0.57149 | 0 | N | 12.68% | 3.935 | 12.68% | N | N
ALDER | Portland | ALDER-YAMHILL | 1118073 | 13 | MULTNOMAH | Y | ALDER WR2 | 28 | 2.5 | 0.86917 | 17.8 | 0.049185 | 0 | N | 5.356% | 0.86917 | 5.356% | N | N
AMITY | near Amity | AMITY-AMITY 13 | 2120013 | 13 | YAMHILL | N | AMITY BR2 | 7.8 | 4.6828 | 0.57206 | 7.4 | 2.0246 | 0 | N | 77.97% | 0.57206 | 77.97% | N | N
AMITY | near Amity | AMITY-BELLEVUE | 2120023 | 13 | YAMHILL | N | AMITY BR1 | 7.5 | 4.67 | 0.975 | 7.8 | 1.6542 | 0 | N | 62.92% | 0.975 | 62.92% | N | N
ARLETA | Portland | ARLETA-52ND | 1125013 | 13 | MULTNOMAH | N | ARLETA BR3 | 16.8 | 9.2 | 3.62 | 14.3 | 0.52098 | 0 | N | 12.58% | 3.62 | 12.58% | N | N
ARLETA | Portland | ARLETA-FOSTER | 1125033 | 13 | MULTNOMAH | N | ARLETA BR2 | 25.2 | 5.7 | 2.6 | 14.3 | 0.2092 | 0 | N | 7.447% | 2.6 | 7.447% | N | N
ARLETA | Portland | ARLETA-HAROLD | 1125023 | 13 | MULTNOMAH | N | ARLETA BR3 | 16.8 | 7.4 | 2.32 | 10 | 0.61884 | 0.042742 | N | 21.06% | 2.2773 | 22.51% | N | N
ARLETA | Portland | ARLETA-POWELL | 1125043 | 13 | MULTNOMAH | N | ARLETA BR2 | 25.2 | 8 | 3.12 | 16.2 | 0.90638 | 0 | N | 22.51% | 3.12 | 22.51% | N | N
ARLETA | Portland | ARLETA-STEELE | 1125053 | 13 | MULTNOMAH | N | ARLETA BR2 | 25.2 | 7.8 | 2.855 | 14.3 | 0.43044 | 0 | N | 13.1% | 2.855 | 13.1% | N | N
BANKS | Banks | BANKS-BANKS 13 | 4135013 | 13 | WASHINGTON | Y | BANKS BR1 | 20 | 2.39 | 0.70786 | 7.3 | 0.20816 | 0 | N | 22.72% | 0.70786 | 22.72% | N | N
BANKS | Banks | BANKS-CEDAR CANYON | 4135023 | 13 | WASHINGTON | Y | BANKS BR1 | 20 | 8.23 | 3.0114 | 17.8 | 0.73917 | 0 | N | 19.71% | 3.0114 | 19.71% | N | N
BARNES | Salem | BARNES-BATTLE CREEK | 2140043 | 13 | MARION | N | BARNES WR2 | 21.2 | 5.4 | 0.775 | 17.8 | 2.7134 | 0 | N | 77.78% | 0.775 | 77.78% | N | N
BARNES | Salem | BARNES-BOONE | 2140013 | 13 | MARION | N | BARNES WR1 | 21.2 | 6.8 | 3.405 | 17.8 | 0.069075 | 0 | N | 1.988% | 3.405 | 1.988% | N | N
BARNES | Salem | BARNES-COMMERCIAL | 2140023 | 13 | MARION | N | BARNES WR1 | 21.2 | 12.5 | 4.725 | 17.8 | 0.68275 | 0 | N | 12.63% | 4.725 | 12.63% | N | N
BARNES | Salem | BARNES-SUNNYSIDE | 2140033 | 13 | MARION | N | BARNES WR2 | 21.2 | 12.2 | 3.01 | 17.8 | 0.8056 | 0 | N | 21.11% | 3.01 | 21.11% | N | N
BEAVERTON | Beaverton | BEAVERTON-ALLEN | 4150013 | 13 | WASHINGTON | Y | BEAVERTON WR2 | 16.8 | 6.4 | 2.3734 | 17.8 | 0.35942 | 0 | N | 13.15% | 2.3734 | 13.15% | Y | N
BEAVERTON | Beaverton | BEAVERTON-JAMIESON | 4150023 | 13 | WASHINGTON | Y | BEAVERTON WR1 | 16.8 | 7.2 | 2.7473 | 17.8 | 0.02961 | 0 | N | 1.066% | 2.7473 | 1.066% | N | N
BEAVERTON | Beaverton | BEAVERTON-NORTHWEST | 4150033 | 13 | WASHINGTON | Y | BEAVERTON WR1 | 16.8 | 4.2 | 1.6452 | 17.8 | 0.1125 | 0 | N | 6.401% | 1.6452 | 6.401% | N | N
BEAVERTON | Beaverton | BEAVERTON-WEST SLOPE | 4150053 | 13 | WASHINGTON | Y | BEAVERTON WR2 | 16.8 | 9.8 | 3.5382 | 17.8 | 0.50134 | 0 | N | 12.41% | 3.5382 | 12.41% | N | N
BELL | near Portland | BELL-BATTIN | 1155073 | 13 | CLACKAMAS | Y | BELL WR2 | 28 | 4.6 | 2.1573 | 18.4 | 0.2504 | 0 | N | 10.4% | 2.1573 | 10.4% | N | N
BELL | near Portland | BELL-BRENTWOOD | 1155083 | 13 | CLACKAMAS | Y | BELL WR1 | 16.8 | 2.3 | 0.94926 | 17.8 | 0.0357 | 0 | N | 3.625% | 0.94926 | 3.625% | N | N
BELL | near Portland | BELL-FLAVEL | 1155023 | 13 | CLACKAMAS | Y | BELL WR2 | 28 | 8.1 | 3.3547 | 17.8 | 0.22132 | 0 | N | 6.189% | 3.3547 | 6.189% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 16.8 | 11.9 | 4.5725 | 17.8 | 0 | 0 | N | 0% | 4.5725 | 0% | Y | N
BELL | near Portland | BELL-KENDALL | 1155053 | 13 | CLACKAMAS | Y | BELL WR2 | 28 | 4.2 | 1.2893 | 17.8 | 0.32721 | 0 | N | 20.24% | 1.2893 | 20.24% | Y | N
BELL | near Portland | BELL-KING | 1155063 | 13 | CLACKAMAS | Y | BELL WR3 | 21 | 9.8 | 3.0075 | 17.8 | 0.39793 | 0 | N | 11.68% | 3.0075 | 11.68% | N | N
BELL | near Portland | BELL-SOUTHGATE | 1155043 | 13 | CLACKAMAS | Y | BELL WR3 | 21 | 9.7 | 3.0472 | 10.7 | 0.23787 | 0 | N | 7.241% | 3.0472 | 7.241% | N | N
BELL | near Portland | BELL-WICHITA | 1155033 | 13 | CLACKAMAS | Y | BELL WR3 | 21 | 6.1 | 1.8303 | 10.7 | 0.35728 | 0 | N | 16.33% | 1.8303 | 16.33% | N | N
BETHANY | Portland | BETHANY-BURTON | 4157043 | 13 | WASHINGTON | Y | BETHANY WR2 | 28 | 9.57 | 1.6049 | 17.8 | 0.7645 | 0 | N | 32.27% | 1.6049 | 32.27% | N | N
BETHANY | Portland | BETHANY-GERMANTOWN | 4157013 | 13 | WASHINGTON | Y | BETHANY WR1 | 28 | 7.17 | 2.0817 | 17.8 | 0.51408 | 0 | N | 19.8% | 2.0817 | 19.8% | N | N
BETHANY | Portland | BETHANY-KAISER | 4157023 | 13 | WASHINGTON | Y | BETHANY WR1 | 28 | 5.43 | 1.0598 | 17.8 | 0.32808 | 0 | N | 23.64% | 1.0598 | 23.64% | N | N
BETHANY | Portland | BETHANY-LAIDLAW | 4157053 | 13 | WASHINGTON | Y | BETHANY WR2 | 28 | 9.77 | 1.7698 | 17.8 | 0.99407 | 0 | N | 35.97% | 1.7698 | 35.97% | N | N
BETHANY | Portland | BETHANY-SPRINGVILLE | 4157063 | 13 | WASHINGTON | Y | BETHANY WR2 | 28 | 4.12 | 0.36517 | 17.8 | 1.7254 | 0 | N | 82.53% | 0.36517 | 82.53% | N | N
BETHANY | Portland | BETHANY-THOMPSON | 4157033 | 13 | WASHINGTON | Y | BETHANY WR1 | 28 | 5.53 | 0.94108 | 17.8 | 0.14396 | 0 | N | 13.27% | 0.94108 | 13.27% | N | N
BETHEL | Salem | BETHEL-FRUITLAND | 2151023 | 13 | MARION | Y | BETHEL WR5 | 28 | 8.2 | 2.7254 | 14.3 | 0.48361 | 0 | N | 15.07% | 2.7254 | 15.07% | N | N
BETHEL | Salem | BETHEL-GEER | 2151033 | 13 | MARION | Y | BETHEL WR5 | 28 | 6.2 | 1.7669 | 14.3 | 0.77507 | 1.75 | Y | 30.49% | 0.0169 | 99.34% | N | N
BETHEL | Salem | BETHEL-MACLEAY | 2151013 | 13 | MARION | Y | BETHEL WR5 | 28 | 4.9 | 1.649 | 17.8 | 0.28331 | 0 | N | 14.66% | 1.649 | 14.66% | N | N
BLUE LAKE | Troutdale | BLUE LAKE-BLUE LAKE 13 | 5156013 | 13 | MULTNOMAH | Y | BLUE LAKE WR1 | 28 | 9.4 | 2.7174 | 17.8 | 0.6316 | 0 | N | 18.86% | 2.7174 | 18.86% | N | N
BLUE LAKE | Troutdale | BLUE LAKE-SUNDIAL | 5156033 | 13 | MULTNOMAH | Y | BLUE LAKE WR1 | 28 | 11.3 | 3.3785 | 18.4 | 0 | 0 | N | 0% | 3.3785 | 0% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 6.5 | 2.123 | 18.4 | 0.21508 | 0 | N | 9.199% | 2.123 | 9.199% | Y | N
BOONES FERRY | Lake Oswego | BOONES FERRY-GOODALL | 1170043 | 13 | CLACKAMAS | Y | BOONES FERRY WR2 | 22 | 6 | 1.8936 | 10.7 | 0.20712 | 0 | N | 9.86% | 1.8936 | 9.86% | N | N
BOONES FERRY | Lake Oswego | BOONES FERRY-KRUSE | 1170013 | 13 | CLACKAMAS | Y | BOONES FERRY WR2 | 22 | 9.7 | 2.8954 | 17.8 | 0.062265 | 0 | N | 2.105% | 2.8954 | 2.105% | N | N
BOONES FERRY | Lake Oswego | BOONES FERRY-LAKE GROVE | 1170033 | 13 | CLACKAMAS | Y | BOONES FERRY WR1 | 28 | 10.6 | 3.8898 | 17.8 | 0.1202 | 0 | N | 2.998% | 3.8898 | 2.998% | N | N
BOONES FERRY | Lake Oswego | BOONES FERRY-MOUNTAIN PARK | 1170053 | 13 | CLACKAMAS | Y | BOONES FERRY WR1 | 28 | 8.5 | 2.5201 | 17.8 | 0.13752 | 0 | N | 5.174% | 2.5201 | 5.174% | N | N
BOONES FERRY | Lake Oswego | BOONES FERRY-WEMBLEY PARK | 1170023 | 13 | CLACKAMAS | Y | BOONES FERRY WR2 | 22 | 6.8 | 2.17 | 17.8 | 0.25268 | 0 | N | 10.43% | 2.17 | 10.43% | N | N
BORING | near Boring | BORING-282ND | 5177033 | 13 | CLACKAMAS | Y | BORING BR2 | 16.8 | 2.3 | 3.1839 | 17.8 | 0.72295 | 0 | N | 18.5% | 3.1839 | 18.5% | N | N
BORING | near Boring | BORING-CITY | 5177023 | 13 | CLACKAMAS | Y | BORING BR2 | 16.8 | 9 | 4.1475 | 17.8 | 5.4164 | 2.9837 | N | 56.63% | 1.1638 | 87.83% | N | N
BORING | near Boring | BORING-TELFORD | 5177013 | 13 | CLACKAMAS | Y | BORING BR1 | 7.5 | 0 | 0 | 17.8 | 0 | 0 | N | 0% | 0 | 0% | N | N
BRIGHTWOOD | Sandy | BRIGHTWOOD-BRIGHTWOOD 13 | 5174013 | 13 | CLACKAMAS | Y | BRIGHTWOOD BR1 | 9.4 | 2.4 | 1.0476 | 10.4 | 0.1804 | 0 | N | 14.69% | 1.0476 | 14.69% | N | Y
BRIGHTWOOD | Sandy | BRIGHTWOOD-NORTH BANK | 5174023 | 13 | CLACKAMAS | Y | BRIGHTWOOD BR1 | 9.4 | 1.9 | -8.8264 | 10.4 | 10.039 | 0 | N | 827.9% | -8.8264 | 827.9% | Y | Y
BROOKWOOD | near Hillsboro | BROOKWOOD-BORWICK | 4185353 | 13 | WASHINGTON | Y | BROOKWOOD WR3 | 50 | 8.32 | 2.6906 | 17.8 | 0.39125 | 0 | N | 12.7% | 2.6906 | 12.7% | Y | Y
BROOKWOOD | near Hillsboro | BROOKWOOD-BROOKWOOD 13 | 4185213 | 13 | WASHINGTON | Y | BROOKWOOD WR2 | 50 | 9.88 | 4.1932 | 18.4 | 0.05893 | 0.175 | N | 1.386% | 4.0182 | 5.501% | Y | Y
BROOKWOOD | near Hillsboro | BROOKWOOD-CRATER | 4185243 | 13 | WASHINGTON | Y | BROOKWOOD WR2 | 50 | 0 | 0 | 18.4 | 0 | 0 | N | 0% | 0 | 0% | Y | Y
BROOKWOOD | near Hillsboro | BROOKWOOD-TRILIUM | 4185323 | 13 | WASHINGTON | Y | BROOKWOOD WR3 | 50 | 7.51 | 2.7472 | 17.8 | 0.02158 | 0 | N | 0.7794% | 2.7472 | 0.7794% | N | Y
BROOKWOOD | near Hillsboro | BROOKWOOD-SUNRISE | 4185313 | 13 | WASHINGTON | Y | BROOKWOOD WR3 | 50 | 11.04 | 4.4444 | 17.8 | 0.81597 | 0 | N | 15.51% | 4.4444 | 15.51% | Y | Y
CANBY | near Barlow | CANBY-13643 | 6190013 | 13 | CLACKAMAS | N | CANBY BR2 | 14 | 0.025 | 0 | 14.3 | 0 | 0 | N | 0% | 0 | 0% | N | N
CANBY | near Barlow | CANBY-13644 | 6190023 | 13 | CLACKAMAS | N | CANBY BR2 | 14 | 2.435 | 0.785 | 7.3 | 0.08811 | 0 | N | 10.09% | 0.785 | 10.09% | N | N
CANBY | near Barlow | CANBY-BUTTEVILLE | 6190043 | 13 | CLACKAMAS | N | CANBY BR4 | 8.4 | 5.785 | 0.93 | 13.7 | 2.5311 | 0 | N | 73.13% | 0.93 | 73.13% | N | N
CANBY | near Barlow | CANBY-FILBERT | 6190033 | 13 | CLACKAMAS | N | CANBY BR1 | 9.4 | 0 | 0 | 14.3 | 0 | 0 | N | 0% | 0 | 0% | N | N
CANBY | near Barlow | CANBY-ZIMMERMAN | 6190053 | 13 | CLACKAMAS | N | CANBY BR3 | 7.5 | 7.65 | 2.35 | 13.7 | 1.6747 | 1.98 | Y | 41.61% | 0.37 | 90.81% | N | N
CANYON | Portland | CANYON-13114 NETWORK #1 | 1196113 | 13 | MULTNOMAH | Y | CANYON WR1 | 50 | 2.2 | 0.4172 | 7 | 0 | 0 | Y | 0% | 0.4172 | 0% | N | N
CANYON | Portland | CANYON-13115 NETWORK #1 | 1196123 | 13 | MULTNOMAH | Y | CANYON WR2 | 50 | 2.4 | 0.78402 | 7 | 0 | 0 | Y | 0% | 0.78402 | 0% | N | N
CANYON | Portland | CANYON-13116 NETWORK #1 | 1196133 | 13 | MULTNOMAH | Y | CANYON WR3 | 50 | 1.8 | 0.65276 | 7 | 0 | 0 | Y | 0% | 0.65276 | 0% | N | N
CANYON | Portland | CANYON-13117 NETWORK #1 | 1196143 | 13 | MULTNOMAH | Y | CANYON WR4 | 50 | 2.4 | 0.67593 | 7 | 0 | 0 | Y | 0% | 0.67593 | 0% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 50 | 1.4 | 0.37746 | 5.6 | 0.05 | 0 | N | 11.7% | 0.37746 | 11.7% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 50 | 3.5 | 1.3515 | 7 | 0 | 0 | N | 0% | 1.3515 | 0% | N | N
CANYON | Portland | CANYON-13120 | 1196043 | 13 | MULTNOMAH | Y | CANYON WR1 | 50 | 4.7 | 2.0546 | 7 | 0 | 0 | N | 0% | 2.0546 | 0% | N | N
CANYON | Portland | CANYON-13121 | 1196453 | 13 | MULTNOMAH | Y | CANYON WR4 | 50 | 1.2 | 0.42386 | 5.6 | 0 | 0 | N | 0% | 0.42386 | 0% | N | N
CANYON | Portland | CANYON-13122 NETWORK #2 | 1196063 | 13 | MULTNOMAH | Y | CANYON WR1 | 50 | 1.8 | 0.60944 | 7.5 | 0.08845 | 0 | Y | 12.67% | 0.60944 | 12.67% | N | N
CANYON | Portland | CANYON-13123 NETWORK #2 | 1196073 | 13 | MULTNOMAH | Y | CANYON WR2 | 50 | 2.2 | 0.85555 | 7.5 | 0.0368 | 0 | Y | 4.124% | 0.85555 | 4.124% | N | N
CANYON | Portland | CANYON-13124 NETWORK #2 | 1196083 | 13 | MULTNOMAH | Y | CANYON WR3 | 50 | 2 | 0.79283 | 7.5 | 0 | 0 | Y | 0% | 0.79283 | 0% | N | N
CANYON | Portland | CANYON-13125 NETWORK #2 | 1196093 | 13 | MULTNOMAH | Y | CANYON WR4 | 50 | 1.6 | 0.538 | 7.5 | 0 | 0 | Y | 0% | 0.538 | 0% | N | N
CANYON | Portland | CANYON-13133 NETWORK #3 | 1196173 | 13 | MULTNOMAH | Y | CANYON WR1 | 50 | 2.5 | 0.69712 | 11.2 | 0 | 0 | Y | 0% | 0.69712 | 0% | N | N
CANYON | Portland | CANYON-13134 NETWORK #3 | 1196183 | 13 | MULTNOMAH | Y | CANYON WR2 | 50 | 4.4 | 1.6326 | 11.2 | 0 | 0 | Y | 0% | 1.6326 | 0% | N | N
CANYON | Portland | CANYON-13135 NETWORK #3 | 1196193 | 13 | MULTNOMAH | Y | CANYON WR3 | 50 | 3.5 | 1.2128 | 11.2 | 0 | 0 | Y | 0% | 1.2128 | 0% | N | N
CANYON | Portland | CANYON-13136 NETWORK #3 | 1196203 | 13 | MULTNOMAH | Y | CANYON WR4 | 50 | 3.6 | 1.0238 | 11.2 | 0 | 0 | Y | 0% | 1.0238 | 0% | N | N
CANYON | Portland | CANYON-21ST | 1196023 | 13 | MULTNOMAH | Y | CANYON WR1 | 50 | 7.1 | 3.3251 | 13.5 | 0 | 0 | N | 0% | 3.3251 | 0% | N | N
CANYON | Portland | CANYON-23RD | 1196103 | 13 | MULTNOMAH | Y | CANYON WR3 | 50 | 8.6 | 3.5244 | 13.5 | 0.096495 | 0 | N | 2.665% | 3.5244 | 2.665% | N | N
CANYON | Portland | CANYON-BURNSIDE | 1196033 | 13 | MULTNOMAH | Y | CANYON WR4 | 50 | 8.5 | 4.1881 | 14.3 | 0.31405 | 0 | N | 6.976% | 4.1881 | 6.976% | N | N
CANYON | Portland | CANYON-CANYON 13 | 1196013 | 13 | MULTNOMAH | Y | CANYON WR2 | 50 | 5.1 | 1.6238 | 17.8 | 0.15065 | 0 | N | 8.49% | 1.6238 | 8.49% | N | N
CARVER | Carver | CARVER-ALMOND | 5198033 | 13 | CLACKAMAS | Y | CARVER WR2 | 28 | 8.8 | 2.586 | 17.8 | 0.33622 | 0 | N | 11.51% | 2.586 | 11.51% | N | N
CARVER | Carver | CARVER-CARVER 13 | 5198013 | 13 | CLACKAMAS | Y | CARVER WR2 | 28 | 10.2 | 4.0097 | 17.8 | 0.49802 | 0 | N | 11.05% | 4.0097 | 11.05% | N | N
CARVER | Carver | CARVER-NORTH | 5198053 | 13 | CLACKAMAS | Y | CARVER WR3 | 28 | 11.7 | 3.034 | 17.8 | 0.57991 | 0 | N | 16.05% | 3.034 | 16.05% | N | N
CARVER | Carver | CARVER-RIVERBEND | 5198023 | 13 | CLACKAMAS | Y | CARVER WR2 | 28 | 6.3 | 2.0641 | 17.8 | 0.49728 | 0 | N | 19.41% | 2.0641 | 19.41% | N | N
CARVER | Carver | CARVER-SOUTH | 5198063 | 13 | CLACKAMAS | Y | CARVER WR3 | 28 | 7.02 | 2.0156 | 17.8 | 0.01452 | 0 | N | 0.7152% | 2.0156 | 0.7152% | N | N
CARVER | Carver | CARVER-WOODS | 5198043 | 13 | CLACKAMAS | Y | CARVER WR3 | 28 | 12.2 | 3.8654 | 17.8 | 1.6265 | 0 | N | 29.62% | 3.8654 | 29.62% | N | N
CEDAR HILLS | near Beaverton | CEDAR HILLS-CEDAR HILLS 13 | 4200033 | 13 | WASHINGTON | Y | CEDAR HILLS WR1 | 28 | 1.33 | 0.21955 | 14.3 | 0 | 0 | N | 0% | 0.21955 | 0% | N | N
CEDAR HILLS | near Beaverton | CEDAR HILLS-LEAHY | 4200063 | 13 | WASHINGTON | Y | CEDAR HILLS WR2 | 28 | 10.71 | 3.7529 | 14.3 | 0.78645 | 0 | N | 17.33% | 3.7529 | 17.33% | N | N
CEDAR HILLS | near Beaverton | CEDAR HILLS-SHOPPING CENTER | 4200013 | 13 | WASHINGTON | Y | CEDAR HILLS WR1 | 28 | 8.03 | 3.072 | 17.8 | 0.31923 | 0 | N | 9.414% | 3.072 | 9.414% | N | N
CEDAR HILLS | near Beaverton | CEDAR HILLS-SKYLINE | 4200043 | 13 | WASHINGTON | Y | CEDAR HILLS WR2 | 28 | 3.16 | 1.2814 | 17.8 | 0.051175 | 0 | N | 3.84% | 1.2814 | 3.84% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 7.59 | 3.5202 | 17.8 | 0.015555 | 0 | N | 0.4399% | 3.5202 | 0.4399% | N | N
CEDAR HILLS | near Beaverton | CEDAR HILLS-SYLVAN | 4200023 | 13 | WASHINGTON | Y | CEDAR HILLS WR2 | 28 | 7.7 | 3.0449 | 17.8 | 0.2855 | 0 | N | 8.573% | 3.0449 | 8.573% | N | N
CENTENNIAL | near Gresham | CENTENNIAL-BARKER | 5202053 | 13 | MULTNOMAH | N | CENTENNIAL WR1 | 22.4 | 8.2 | 3.53 | 14.3 | 0.2472 | 0 | N | 6.545% | 3.53 | 6.545% | N | N
CENTENNIAL | near Gresham | CENTENNIAL-BRAECROFT | 5202043 | 13 | MULTNOMAH | N | CENTENNIAL WR2 | 16.8 | 4.9 | 1.81 | 17.8 | 0.25162 | 0 | N | 12.21% | 1.81 | 12.21% | N | N
CENTENNIAL | near Gresham | CENTENNIAL-CENTENNIAL 13 | 5202033 | 13 | MULTNOMAH | N | CENTENNIAL WR1 | 22.4 | 9.2 | 3.9733 | 14.3 | 0.61078 | 0 | N | 13.32% | 3.9733 | 13.32% | N | N
CENTENNIAL | near Gresham | CENTENNIAL-TREELAND | 5202063 | 13 | MULTNOMAH | N | CENTENNIAL WR2 | 16.8 | 8.4 | 3.3325 | 14.3 | 0.26222 | 0 | N | 7.295% | 3.3325 | 7.295% | N | N
CLACKAMAS | Clackamas | CLACKAMAS-EVELYN | 6205023 | 13 | CLACKAMAS | Y | CLACKAMAS WR1 | 15 | 4.7 | 1.5451 | 17.8 | 0.04637 | 0 | N | 2.914% | 1.5451 | 2.914% | N | N
CLACKAMAS | Clackamas | CLACKAMAS-GLADSTONE | 6205013 | 13 | CLACKAMAS | Y | CLACKAMAS WR1 | 15 | 8.4 | 2.4575 | 17.8 | 0.53405 | 0 | N | 17.85% | 2.4575 | 17.85% | N | N
CLACKAMAS | Clackamas | CLACKAMAS-JENNIFER | 6205033 | 13 | CLACKAMAS | Y | CLACKAMAS WR2 | 25.5 | 6.29 | 2.2431 | 17.8 | 0 | 0 | N | 0% | 2.2431 | 0% | N | N
CLACKAMAS | Clackamas | CLACKAMAS-TOLBERT | 6205043 | 13 | CLACKAMAS | Y | CLACKAMAS WR2 | 25.5 | 14 | 4.9088 | 17.8 | 0.54341 | 0 | N | 9.967% | 4.9088 | 9.967% | N | N
CLAXTAR | Salem | CLAXTAR-CLAXTAR 13 | 2207013 | 13 | MARION | N | CLAXTAR BR1 | 28 | 4.3 | 2.18 | 14.3 | 0.01485 | 0 | N | 0.6766% | 2.18 | 0.6766% | N | N
CLAXTAR | Salem | CLAXTAR-HAYESVILLE | 2207023 | 13 | MARION | N | CLAXTAR BR1 | 28 | 6 | 2.695 | 17.8 | 0.12921 | 0 | N | 4.575% | 2.695 | 4.575% | N | N
CLAXTAR | Salem | CLAXTAR-RIDGE | 2207033 | 13 | MARION | N | CLAXTAR BR1 | 28 | 6.9 | 1.8 | 17.8 | 0.5676 | 0 | N | 23.97% | 1.8 | 23.97% | N | N
COFFEE CREEK | Sherwood | COFFEE CREEK-FREEMAN | 4209023 | 13 | WASHINGTON | Y | COFFEE CREEK WR1 | 28 | 9.9 | 2.3439 | 17.8 | 0.0136 | 0 | N | 0.5769% | 2.3439 | 0.5769% | N | N
COFFEE CREEK | Sherwood | COFFEE CREEK-HOLIDAY | 4209013 | 13 | WASHINGTON | Y | COFFEE CREEK WR1 | 28 | 6.9 | 2.074 | 17.8 | 0.11621 | 0 | N | 5.306% | 2.074 | 5.306% | N | N
COLTON | Colton | COLTON-DHOOGHE | 6208013 | 13 | CLACKAMAS | Y | COLTON BR1 | 7.5 | 2.2893 | -1.2953 | 5 | 2.3418 | 0 | Y | 223.8% | -1.2953 | 223.8% | N | N
COLTON | Colton | COLTON-GRAYS HILL | 6208023 | 13 | CLACKAMAS | Y | COLTON BR1 | 7.5 | 3.6018 | 1.6326 | 10.4 | 0.12942 | 0 | Y | 7.345% | 1.6326 | 7.345% | N | N
CORNELIUS | Cornelius | CORNELIUS-ADAIR | 4210033 | 13 | WASHINGTON | Y | CORNELIUS BR1 | 28 | 6.75 | 2.6082 | 17.8 | 0.54891 | 0 | N | 17.39% | 2.6082 | 17.39% | N | N
CORNELIUS | Cornelius | CORNELIUS-CORNELIUS 13 | 4210013 | 13 | WASHINGTON | Y | CORNELIUS BR1 | 28 | 9.73 | 3.8274 | 14.3 | 0.7211 | 0 | N | 15.85% | 3.8274 | 15.85% | N | N
CORNELIUS | Cornelius | CORNELIUS-VERBOORT | 4210023 | 13 | WASHINGTON | Y | CORNELIUS BR1 | 28 | 6.24 | -0.64156 | 14.3 | 3.5293 | 0 | N | 122.2% | -0.64156 | 122.2% | Y | N
CORNELL | Portland | CORNELL-BLUFFS | 4206023 | 13 | WASHINGTON | Y | CORNELL WR1 | 28 | 11.92 | 3.4555 | 17.8 | 0.74877 | 0 | N | 17.81% | 3.4555 | 17.81% | N | N
CORNELL | Portland | CORNELL-SALTZMAN | 4206013 | 13 | WASHINGTON | Y | CORNELL WR1 | 28 | 5.15 | 2.1093 | 17.8 | 0.078788 | 0 | N | 3.601% | 2.1093 | 3.601% | N | N
CORNELL | Portland | CORNELL-WESTLAWN | 4206033 | 13 | WASHINGTON | Y | CORNELL WR1 | 28 | 7.95 | 3.2721 | 17.8 | 0.3535 | 0 | N | 9.75% | 3.2721 | 9.75% | N | N
CULVER | Salem | CULVER-CULVER 13 | 2211143 | 13 | MARION | Y | CULVER WR1 | 28 | 1.6 | 0.16749 | 17.8 | 0.052795 | 0 | N | 23.97% | 0.16749 | 23.97% | N | N
CULVER | Salem | CULVER-GAFFIN | 2211113 | 13 | MARION | Y | CULVER WR1 | 28 | 1.6 | 0.19992 | 17.8 | 0 | 0 | N | 0% | 0.19992 | 0% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 0 | 0.045177 | 24.9 | 0 | 0 | N | 0% | 0.045177 | 0% | N | N
CURTIS | Portland | CURTIS-11077 | 1212012 | 11.1 | MULTNOMAH | Y | CURTIS WR1 | 16.8 | 2.5 | 0.73895 | 8.9 | 0.05375 | 0 | N | 6.781% | 0.73895 | 6.781% | N | N
CURTIS | Portland | CURTIS-CURTIS 13 | 1212013 | 13 | MULTNOMAH | Y | CURTIS WR1 | 16.8 | 2.9 | 0.95136 | 14.3 | 0.12783 | 0 | N | 11.84% | 0.95136 | 11.84% | N | N
DAYTON | near Dayton | DAYTON-EAST | 4220013 | 13 | YAMHILL | Y | DAYTON BR1 | 7.5 | 6.6641 | 2.2118 | 10.4 | 1.2079 | 1.8 | Y | 35.32% | 0.41181 | 87.96% | N | N
DAYTON | near Dayton | DAYTON-LAFAYETTE | 4220033 | 13 | YAMHILL | Y | DAYTON BR3 | 14 | 7.2338 | 2.1869 | 7.4 | 0.83917 | 0 | N | 27.73% | 2.1869 | 27.73% | N | Y
DAYTON | near Dayton | DAYTON-SOUTHWEST | 4220023 | 13 | YAMHILL | Y | DAYTON BR3 | 14 | 3.5759 | -3.6411 | 17.8 | 5.0417 | 0 | N | 360% | -3.6411 | 360% | Y | Y
DELAWARE | Portland | DELAWARE-DENVER | 1221013 | 13 | MULTNOMAH | Y | DELAWARE WR1 | 22.4 | 8.3 | 3.0494 | 9.9 | 0.45203 | 0 | N | 12.91% | 3.0494 | 12.91% | N | N
DELAWARE | Portland | DELAWARE-INTERSTATE | 1221023 | 13 | MULTNOMAH | Y | DELAWARE WR1 | 22.4 | 5.4 | 2.07 | 17.8 | 0.43706 | 0 | N | 17.43% | 2.07 | 17.43% | N | N
DELAWARE | Portland | DELAWARE-LOMBARD | 1221033 | 13 | MULTNOMAH | Y | DELAWARE WR1 | 22.4 | 11.5 | 4.6495 | 17.8 | 0.36043 | 0 | N | 7.194% | 4.6495 | 7.194% | N | N
DENNY | Beaverton | DENNY-EAST | 4222043 | 13 | WASHINGTON | Y | DENNY WR2 | 28 | 6 | 2.2443 | 17.8 | 0.26547 | 0 | N | 10.58% | 2.2443 | 10.58% | N | N
DENNY | Beaverton | DENNY-NORTH | 4222013 | 13 | WASHINGTON | Y | DENNY WR1 | 28 | 10 | 2.6799 | 17.8 | 0.1529 | 0 | N | 5.397% | 2.6799 | 5.397% | N | N
DENNY | Beaverton | DENNY-SOUTH | 4222033 | 13 | WASHINGTON | Y | DENNY WR2 | 28 | 9.5 | 3.0324 | 17.8 | 0.52923 | 0 | N | 14.86% | 3.0324 | 14.86% | N | N
DENNY | Beaverton | DENNY-WEST | 4222023 | 13 | WASHINGTON | Y | DENNY WR1 | 28 | 7.7 | 2.1456 | 17.8 | 0.70258 | 0 | N | 24.67% | 2.1456 | 24.67% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 12.5 | 5.71 | 1.6172 | 11 | 0 | 0 | N | 0% | 1.6172 | 0% | N | N
DILLEY | near Forest Grove | DILLEY-DILLEY 13 | 4223013 | 13 | WASHINGTON | Y | DILLEY BR1 | 12.5 | 3.52 | 1.3819 | 17.8 | 0.2825 | 0 | N | 16.97% | 1.3819 | 16.97% | N | N
DUNNS CORNER | near Sandy | DUNNS CORNER-DUNNS CORNER 13 | 5218013 | 13 | CLACKAMAS | Y | DUNNS CORNER BR1 | 14 | 9.2 | 0.0025741 | 17.8 | 7.1473 | 1.85 | N | 99.96% | -1.8474 | 125.8% | Y | Y
DUNNS CORNER | near Sandy | DUNNS CORNER-KELSO | 5218023 | 13 | CLACKAMAS | Y | DUNNS CORNER BR1 | 14 | 2.9 | 0.61086 | 17.8 | 0.11414 | 2.489 | N | 15.74% | -1.8781 | 359.1% | Y | Y
DURHAM | Tigard | DURHAM-BONITA | 4224043 | 13 | WASHINGTON | Y | DURHAM WR4 | 28 | 9.3 | 2.8069 | 17.8 | 0.19173 | 0 | N | 6.394% | 2.8069 | 6.394% | N | N
DURHAM | Tigard | DURHAM-BRIDGEPORT | 4224053 | 13 | WASHINGTON | Y | DURHAM WR4 | 28 | 8.6 | 2.765 | 17.8 | 0.27737 | 0 | N | 9.117% | 2.765 | 9.117% | N | N
DURHAM | Tigard | DURHAM-DURHAM 13 | 4224013 | 13 | WASHINGTON | Y | DURHAM WR3 | 28 | 10.2 | 2.8598 | 17.8 | 0.002 | 0 | N | 0.06989% | 2.8598 | 0.06989% | N | N
DURHAM | Tigard | DURHAM-SATTLER | 4224023 | 13 | WASHINGTON | Y | DURHAM WR3 | 28 | 7.9 | 2.0453 | 17.8 | 0.52811 | 0 | N | 20.52% | 2.0453 | 20.52% | N | N
DURHAM | Tigard | DURHAM-SOUTH | 4224033 | 13 | WASHINGTON | Y | DURHAM WR4 | 28 | 3.5 | 1.5151 | 17.8 | 0 | 0 | N | 0% | 1.5151 | 0% | N | N
E | Portland | E-11021 | 1225012 | 11.1 | MULTNOMAH | Y | E WK1-2-3 | 62.4 | 0.5 | 0.022947 | 11.9 | 0 | 0 | N | 0% | 0.022947 | 0% | N | Y
E | Portland | E-11039 | 1225022 | 11.1 | MULTNOMAH | Y | E WK27 | 70 | 4.5 | 0.14984 | 16 | 0 | 0 | N | 0% | 0.14984 | 0% | N | Y
E | Portland | E-11040 | 1225032 | 11.1 | MULTNOMAH | Y | E WK1-2-3 | 62.4 | 4.3 | 1.1482 | 8.9 | 0.20737 | 0 | N | 15.3% | 1.1482 | 15.3% | N | Y
E | Portland | E-11041 | 1225042 | 11.1 | MULTNOMAH | Y | E WK1-2-3 | 62.4 | 3.3 | 0.84007 | 11.9 | 0.189 | 0 | N | 18.37% | 0.84007 | 18.37% | N | Y
E | Portland | E-11042 | 1225052 | 11.1 | MULTNOMAH | Y | E WK27 | 70 | 4.7 | 0.09345 | 9.4 | 0 | 0 | N | 0% | 0.09345 | 0% | N | Y
E | Portland | E-11043 | 1225062 | 11.1 | MULTNOMAH | Y | E WK1-2-3 | 62.4 | 3.1 | 0.78573 | 8.9 | 0.1272 | 0 | N | 13.93% | 0.78573 | 13.93% | N | Y
E | Portland | E-11047 | 1225112 | 11.1 | MULTNOMAH | Y | E WK1-2-3 | 62.4 | 5 | 1.0091 | 11.2 | 0.1474 | 0 | N | 12.75% | 1.0091 | 12.75% | N | Y
E | Portland | E-11064 | 1225122 | 11.1 | MULTNOMAH | Y | E WK1-2-3 | 62.4 | 0.8 | 0.030789 | 11.9 | 0.0099 | 0 | N | 24.33% | 0.030789 | 24.33% | N | Y
E | Portland | E-13139 | 1225013 | 13 | MULTNOMAH | Y | E WR13-14-15 | 62.4 | 4.7 | 2.2061 | 17.8 | 0.00995 | 0 | N | 0.449% | 2.2061 | 0.449% | N | Y
E | Portland | E-13140 | 1225023 | 13 | MULTNOMAH | Y | E WR13-14-15 | 62.4 | 8 | 2.9849 | 13.7 | 0.02041 | 0 | N | 0.6791% | 2.9849 | 0.6791% | N | Y
E | Portland | E-13141 | 1225033 | 13 | MULTNOMAH | Y | E WR4 | 70 | 5.9 | 2.327 | 13.9 | 0 | 0 | N | 0% | 2.327 | 0% | N | Y
E | Portland | E-13142 | 1225093 | 13 | MULTNOMAH | Y | E WR13-14-15 | 62.4 | 8.1 | 3.8087 | 13.7 | 0.06045 | 0 | N | 1.562% | 3.8087 | 1.562% | Y | Y
E | Portland | E-13144 | 1225083 | 13 | MULTNOMAH | Y | E WR4 | 70 | 7.9 | 2.4285 | 17.8 | 0.97172 | 0 | N | 28.58% | 2.4285 | 28.58% | N | Y
E | Portland | E-13145 | 1225043 | 13 | MULTNOMAH | Y | E WR13-14-15 | 62.4 | 6.4 | 3.165 | 13.7 | 0.01832 | 0 | N | 0.5755% | 3.165 | 0.5755% | N | Y
E | Portland | E-13148 | 1225053 | 13 | MULTNOMAH | Y | E WR4 | 70 | 5.6 | 2.2513 | 13.9 | 0.0404 | 0 | N | 1.763% | 2.2513 | 1.763% | N | Y
E | Portland | E-13149 | 1225063 | 13 | MULTNOMAH | Y | E WR13-14-15 | 62.4 | 7.5 | 3.3973 | 13.7 | 0.18948 | 0 | N | 5.283% | 3.3973 | 5.283% | N | Y
E | Portland | E-13150 | 1225073 | 13 | MULTNOMAH | Y | E WR4 | 70 | 10.6 | 3.7428 | 14.3 | 0.17292 | 0 | N | 4.416% | 3.7428 | 4.416% | N | Y
EAGLE CREEK | Eagle Creek | EAGLE CREEK-BARTON | 5230013 | 13 | CLACKAMAS | N | EAGLE CREEK BR1 | 14 | 3 | 1.3497 | 10.4 | 0.14439 | 0 | N | 9.664% | 1.3497 | 9.664% | N | N
EAGLE CREEK | Eagle Creek | EAGLE CREEK-RIVER MILL | 5230023 | 13 | CLACKAMAS | N | EAGLE CREEK BR1 | 14 | 5 | 1.78 | 10.7 | 0.22495 | 0 | N | 11.22% | 1.78 | 11.22% | N | N
EASTPORT | Portland | EASTPORT-76TH | 1231023 | 13 | MULTNOMAH | Y | EASTPORT WR1 | 16.8 | 8.4 | 3.2993 | 10.4 | 0.28584 | 0 | N | 7.973% | 3.2993 | 7.973% | N | N
EASTPORT | Portland | EASTPORT-PLAZA | 1231013 | 13 | MULTNOMAH | Y | EASTPORT WR1 | 16.8 | 6.6 | 2.9248 | 17.8 | 0.06467 | 0 | N | 2.163% | 2.9248 | 2.163% | N | N
ELMA | near Salem | ELMA-ELMA 13 | 2233013 | 13 | MARION | Y | ELMA BR1 | 28 | 3.3 | 1.0642 | 17.8 | 0.14731 | 0 | N | 12.16% | 1.0642 | 12.16% | N | N
ELMA | near Salem | ELMA-FOUR CORNERS | 2233023 | 13 | MARION | Y | ELMA BR1 | 28 | 9.9 | 3.6978 | 14.3 | 0.25517 | 0 | N | 6.455% | 3.6978 | 6.455% | N | N
ELMA | near Salem | ELMA-HUDSON | 2233043 | 13 | MARION | Y | ELMA BR2 | 28 | 10.2 | 3.6552 | 14.3 | 0.29486 | 0 | N | 7.465% | 3.6552 | 7.465% | N | N
ELMA | near Salem | ELMA-STATE | 2233033 | 13 | MARION | Y | ELMA BR2 | 28 | 6.7 | 2.6234 | 17.8 | 0.97742 | 0 | N | 27.14% | 2.6234 | 27.14% | N | N
ESTACADA | Estacada | ESTACADA-ESTACADA 13 | 5237023 | 13 | CLACKAMAS | Y | ESTACADA BR1 | 14 | 6.3 | -6.1734 | 18.4 | 10.3591 | 2.672 | N | 247.5% | -8.8454 | 311.3% | Y | Y
ESTACADA | Estacada | ESTACADA-FARADAY | 5237013 | 13 | CLACKAMAS | Y | ESTACADA BR2 | 15.6 | 9 | 3.4066 | 17.8 | 1.0324 | 0 | N | 23.26% | 3.4066 | 23.26% | N | N
ESTACADA | Estacada | ESTACADA-NORTH FORK | 5237033 | 13 | CLACKAMAS | Y | ESTACADA BR1 | 14 | 5.4 | 0.49496 | 17.8 | 2.4434 | 0 | N | 83.16% | 0.49496 | 83.16% | Y | Y
FAIRMOUNT | Salem | FAIRMOUNT-CANDALARIA | 2250013 | 13 | MARION | N | FAIRMOUNT WR1 | 25 | 9 | 3.325 | 17.8 | 0.46646 | 0 | N | 12.3% | 3.325 | 12.3% | N | N
FAIRMOUNT | Salem | FAIRMOUNT-MISSION | 2250023 | 13 | MARION | N | FAIRMOUNT WR1 | 25 | 10 | 3.17 | 17.8 | 0.66393 | 0 | N | 17.32% | 3.17 | 17.32% | N | N
FAIRVIEW | Fairview | FAIRVIEW-CLEAR CREEK | 5251033 | 13 | MULTNOMAH | Y | FAIRVIEW WR2 | 22.4 | 2.3 | 0.93414 | 18.4 | 0 | 0 | N | 0% | 0.93414 | 0% | N | Y
FAIRVIEW | Fairview | FAIRVIEW-FAIRVIEW 13 | 5251053 | 13 | MULTNOMAH | Y | FAIRVIEW WR1 | 22.4 | 7.1 | 2.4314 | 17.8 | 0.13167 | 0 | N | 5.137% | 2.4314 | 5.137% | N | Y
FAIRVIEW | Fairview | FAIRVIEW-KENNEL CLUB | 5251013 | 13 | MULTNOMAH | Y | FAIRVIEW WR2 | 22.4 | 5.2 | 1.9153 | 17.8 | 0.09948 | 0 | N | 4.938% | 1.9153 | 4.938% | N | Y
FAIRVIEW | Fairview | FAIRVIEW-TROUTDALE | 5251043 | 13 | MULTNOMAH | Y | FAIRVIEW WR1 | 22.4 | 11.6 | 4.6537 | 17.8 | 1.4284 | 0 | N | 23.48% | 4.6537 | 23.48% | N | Y
FAIRVIEW | Fairview | FAIRVIEW-WOOD VILLAGE | 5251023 | 13 | MULTNOMAH | Y | FAIRVIEW WR1 | 22.4 | 2.5 | 0.70231 | 17.8 | 0.11143 | 0 | N | 13.69% | 0.70231 | 13.69% | N | Y
FARGO | Aurora | FARGO-FARGO 13 | 2253013 | 13 | MARION | N | FARGO WR1 | 8.4 | 8.1 | 1.41 | 17.8 | 2.2889 | 0 | N | 61.88% | 1.41 | 61.88% | N | N
GALES CREEK | Forest Grove | GALES CREEK-GALES CREEK 13 | 4275013 | 13 | WASHINGTON | Y | GALES CREEK BR1 | 3 | 2.17 | 0.86175 | 5.5 | 0.2531 | 0 | N | 22.7% | 0.86175 | 22.7% | N | N
GARDEN HOME | near Portland | GARDEN HOME-MCKAY | 4276023 | 13 | WASHINGTON | Y | GARDEN HOME WR2 | 21 | 7.7 | 2.3542 | 17.8 | 0.42701 | 0 | N | 15.35% | 2.3542 | 15.35% | N | N
GARDEN HOME | near Portland | GARDEN HOME-METZGER | 4276013 | 13 | WASHINGTON | Y | GARDEN HOME WR2 | 21 | 10.6 | 3.5768 | 17.8 | 0.32861 | 0 | N | 8.414% | 3.5768 | 8.414% | N | N
GLENCOE | Portland | GLENCOE-GLISAN | 1277013 | 13 | MULTNOMAH | N | GLENCOE WR1 | 25 | 11.4 | 3.035 | 9.9 | 0.4162 | 0 | N | 12.06% | 3.035 | 12.06% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | N | *REDACTED* | 25 | 1.8 | 0.705 | 9.9 | 0.026505 | 0 | N | 3.623% | 0.705 | 3.623% | N | N
GLENCOE | Portland | GLENCOE-SUNNYSIDE | 1277033 | 13 | MULTNOMAH | N | GLENCOE WR1 | 25 | 8.2 | 2.54 | 17.8 | 0.52693 | 0 | N | 17.18% | 2.54 | 17.18% | N | N
GLENCULLEN | Portland | GLENCULLEN-BRIDLEMILE | 1278013 | 13 | MULTNOMAH | N | GLENCULLEN WR1 | 24 | 7.6 | 2.72 | 17.8 | 0.5076 | 0 | N | 15.73% | 2.72 | 15.73% | N | N
GLENCULLEN | Portland | GLENCULLEN-SUNSET | 1278023 | 13 | MULTNOMAH | N | GLENCULLEN WR1 | 24 | 6 | 2.19 | 17.8 | 0.28847 | 0 | N | 11.64% | 2.19 | 11.64% | N | N
GLENDOVEER | near Portland | GLENDOVEER-13596 | 5280013 | 13 | MULTNOMAH | Y | GLENDOVEER WR2 | 22.4 | 5.4 | 1.8504 | 17.8 | 0.046471 | 0 | N | 2.45% | 1.8504 | 2.45% | N | Y
GLENDOVEER | near Portland | GLENDOVEER-13597 | 5280023 | 13 | MULTNOMAH | Y | GLENDOVEER WR2 | 22.4 | 4.5 | 1.7745 | 17.8 | 0.04137 | 0 | N | 2.278% | 1.7745 | 2.278% | N | Y
GLENDOVEER | near Portland | GLENDOVEER-13598 | 5280033 | 13 | MULTNOMAH | Y | GLENDOVEER WR4 | 28 | 6.1 | 2.3196 | 17.8 | 0.19281 | 0 | N | 7.674% | 2.3196 | 7.674% | N | Y
GLENDOVEER | near Portland | GLENDOVEER-13599 | 5280043 | 13 | MULTNOMAH | Y | GLENDOVEER WR2 | 22.4 | 5 | 1.7677 | 17.8 | 0.77014 | 0 | N | 30.35% | 1.7677 | 30.35% | N | Y
GLENDOVEER | near Portland | GLENDOVEER-CLIFFGATE | 5280053 | 13 | MULTNOMAH | Y | GLENDOVEER WR4 | 28 | 8.4 | 2.5453 | 17.8 | 0.33805 | 0 | N | 11.72% | 2.5453 | 11.72% | N | Y
GLENDOVEER | near Portland | GLENDOVEER-NORTHEAST | 5280063 | 13 | MULTNOMAH | Y | GLENDOVEER WR4 | 28 | 5 | 1.4098 | 17.8 | 0.11088 | 0 | N | 7.292% | 1.4098 | 7.292% | N | Y
GRAND RONDE | Grand Ronde | GRAND RONDE-AGENCY | 2285033 | 13 | POLK | Y | GRAND RONDE WR2 | 12.5 | 1.8738 | 0.7918 | 7.8 | 0.15674 | 0 | N | 16.52% | 0.7918 | 16.52% | N | Y
GRAND RONDE | Grand Ronde | GRAND RONDE-FORTHILL | 2285023 | 13 | POLK | Y | GRAND RONDE WR2 | 12.5 | 4.8 | 1.0053 | 10.4 | 2.2606 | 2.565 | N | 69.22% | -1.5597 | 147.8% | Y | Y
HARBORTON | near Portland | HARBORTON-BURLINGTON | 1310023 | 13 | MULTNOMAH | Y | HARBORTON WR3 | 28 | 4.9 | 1.6252 | 10.4 | 0.22239 | 0 | N | 12.04% | 1.6252 | 12.04% | Y | Y
HARBORTON | near Portland | HARBORTON-HARBORTON 13 | 1310013 | 13 | MULTNOMAH | Y | HARBORTON WR3 | 28 | 0.7 | 0.23563 | 13.7 | 0 | 0 | N | 0% | 0.23563 | 0% | Y | Y
HARBORTON | near Portland | HARBORTON-LINNTON | 1310033 | 13 | MULTNOMAH | Y | HARBORTON WR4 | 28 | 2.7 | 0.78783 | 10.4 | 0.00712 | 0 | N | 0.8956% | 0.78783 | 0.8956% | Y | Y
HARMONY | near Milwaukie | HARMONY-HARMONY 13 | 1313013 | 13 | CLACKAMAS | Y | HARMONY WR1 | 28 | 9.1 | 3.4414 | 17.8 | 0.35645 | 0 | N | 9.386% | 3.4414 | 9.386% | N | N
HARMONY | near Milwaukie | HARMONY-INTERNATIONAL | 1313053 | 13 | CLACKAMAS | Y | HARMONY WR2 | 21 | 6.6 | 2.0001 | 17.8 | 0.90035 | 0 | N | 31.04% | 2.0001 | 31.04% | N | N
HARMONY | near Milwaukie | HARMONY-LAKE | 6313033 | 13 | CLACKAMAS | Y | HARMONY WR1 | 28 | 9.9 | 3.8531 | 17.8 | 0.23931 | 0 | N | 5.848% | 3.8531 | 5.848% | N | N
HARMONY | near Milwaukie | HARMONY-LINWOOD | 1313033 | 13 | CLACKAMAS | Y | HARMONY WR2 | 21 | 6.5 | 2.5007 | 14.3 | 0.66499 | 0 | N | 21.01% | 2.5007 | 21.01% | N | N
HARMONY | near Milwaukie | HARMONY-MILWAUKIE | 1313023 | 13 | CLACKAMAS | Y | HARMONY WR1 | 28 | 6.8 | 1.5833 | 14.3 | 0.60647 | 0 | N | 27.69% | 1.5833 | 27.69% | N | N
HARMONY | near Milwaukie | HARMONY-THIESSEN | 1313043 | 13 | CLACKAMAS | Y | HARMONY WR2 | 21 | 5.3 | 1.8986 | 17.8 | 0.2712 | 0 | N | 12.5% | 1.8986 | 12.5% | N | N
HARRISON | Portland | HARRISON-DAVIS | 1312043 | 13 | MULTNOMAH | Y | HARRISON WR1 | 28 | 8.9 | 3.3768 | 14.3 | 0.31001 | 0 | N | 8.408% | 3.3768 | 8.408% | Y | Y
HARRISON | Portland | HARRISON-HARRISON 13 | 1312053 | 13 | MULTNOMAH | Y | HARRISON WR1 | 28 | 9 | 3.365 | 17.8 | 0.21116 | 0 | N | 5.905% | 3.365 | 5.905% | Y | Y
HARRISON | Portland | HARRISON-IVON | 1312013 | 13 | MULTNOMAH | Y | HARRISON WR1 | 28 | 6 | 2.7587 | 13.7 | 0.06839 | 0 | N | 2.419% | 2.7587 | 2.419% | Y | Y
HAYDEN ISLAND | near Portland | HAYDEN ISLAND-MAINLAND | 1316033 | 13 | MULTNOMAH | Y | HAYDEN ISLAND WR1 | 16.8 | 6.1 | 1.541 | 13.5 | 0 | 0 | N | 0% | 1.541 | 0% | N | N
HAYDEN ISLAND | near Portland | HAYDEN ISLAND-NORTH SHORE | 1316013 | 13 | MULTNOMAH | Y | HAYDEN ISLAND WR2 | 16.8 | 6.4 | 2.9225 | 14.3 | 0.04035 | 0 | N | 1.362% | 2.9225 | 1.362% | N | N
HAYDEN ISLAND | near Portland | HAYDEN ISLAND-SOUTH SHORE | 1316023 | 13 | MULTNOMAH | Y | HAYDEN ISLAND WR1 | 16.8 | 3.7 | 1.2528 | 14.3 | 0.31378 | 0 | N | 20.03% | 1.2528 | 20.03% | N | N
HEMLOCK | Portland | HEMLOCK-FREMONT | 5317023 | 13 | MULTNOMAH | Y | HEMLOCK WR1 | 28 | 4.6 | 1.1067 | 17.8 | 0.060605 | 0 | N | 5.192% | 1.1067 | 5.192% | N | N
HEMLOCK | Portland | HEMLOCK-HEMLOCK 13 | 5317013 | 13 | MULTNOMAH | Y | HEMLOCK WR1 | 28 | 10.9 | 4.4719 | 17.8 | 0.07296 | 0 | N | 1.605% | 4.4719 | 1.605% | N | N
HEMLOCK | Portland | HEMLOCK-MASON | 5317033 | 13 | MULTNOMAH | Y | HEMLOCK WR1 | 28 | 10.9 | 2.7463 | 17.8 | 1.4345 | 0 | N | 34.31% | 2.7463 | 34.31% | N | N
HILLCREST | Salem | HILLCREST-CASCADIA | 2318033 | 13 | MARION | Y | HILLCREST WR1 | 28 | 0.6 | 0.08725 | 24.9 | 0 | 0 | N | 0% | 0.08725 | 0% | N | Y
HILLCREST | Salem | HILLCREST-HILLCREST 13 | 2318023 | 13 | MARION | Y | HILLCREST WR1 | 28 | 5.9 | 1.1519 | 11 | 0.19656 | 0 | N | 14.58% | 1.1519 | 14.58% | N | Y
HILLCREST | Salem | HILLCREST-REED | 2318043 | 13 | MARION | Y | HILLCREST WR1 | 28 | 0.1 | 0 | 17.8 | 0 | 0 | N | 0% | 0 | 0% | N | Y
HILLCREST | Salem | HILLCREST-SOUTH | 2318223 | 13 | MARION | Y | HILLCREST WR1 | 28 | 5.5 | 0.95669 | 18.4 | 0.17865 | 0 | N | 15.74% | 0.95669 | 15.74% | N | Y
HILLSBORO | Hillsboro | HILLSBORO-DAIRY CREEK | 4320013 | 13 | WASHINGTON | Y | HILLSBORO BR2 | 22.4 | 12.9 | 2.6324 | 17.8 | 2.1822 | 0 | N | 45.32% | 2.6324 | 45.32% | N | N
HILLSBORO | Hillsboro | HILLSBORO-DENNIS | 4320053 | 13 | WASHINGTON | Y | HILLSBORO BR2 | 22.4 | 3.9 | 1.5859 | 10.7 | 0.1064 | 0 | N | 6.287% | 1.5859 | 6.287% | N | N
HILLSBORO | Hillsboro | HILLSBORO-JACKSON | 4320033 | 13 | WASHINGTON | Y | HILLSBORO BR1 | 21 | 10.3 | 2.7263 | 14.3 | 0.97337 | 0 | N | 26.31% | 2.7263 | 26.31% | N | N
HILLSBORO | Hillsboro | HILLSBORO-LAUREL | 4320023 | 13 | WASHINGTON | Y | HILLSBORO BR1 | 21 | 8.93 | 3.4515 | 14.3 | 1.1464 | 0 | N | 24.93% | 3.4515 | 24.93% | N | N
HILLSBORO | Hillsboro | HILLSBORO-SCHOLLS | 4320043 | 13 | WASHINGTON | Y | HILLSBORO BR2 | 22.4 | 6.86 | 2.4811 | 17.8 | 0.10129 | 0 | N | 3.922% | 2.4811 | 3.922% | N | N
HOGAN NORTH | Gresham | HOGAN NORTH-BRIGADOON | 5323023 | 13 | MULTNOMAH | Y | HOGAN NORTH WR2 | 28 | 9.2 | 2.8868 | 17.8 | 0.34875 | 0 | N | 10.78% | 2.8868 | 10.78% | N | N
HOGAN NORTH | Gresham | HOGAN NORTH-HOGAN NORTH 13 | 5323043 | 13 | MULTNOMAH | Y | HOGAN NORTH WR1 | 28 | 13.8 | 4.9893 | 17.8 | 0.58191 | 0 | N | 10.44% | 4.9893 | 10.44% | N | N
HOGAN NORTH | Gresham | HOGAN NORTH-LINKS | 5323033 | 13 | MULTNOMAH | Y | HOGAN NORTH WR1 | 28 | 11 | 3.7811 | 17.8 | 0.36266 | 0 | N | 8.752% | 3.7811 | 8.752% | N | N
HOGAN NORTH | Gresham | HOGAN NORTH-SALQUIST | 5323013 | 13 | MULTNOMAH | Y | HOGAN NORTH WR2 | 28 | 9.6 | 3.3563 | 14.3 | 0.42092 | 0 | N | 11.14% | 3.3563 | 11.14% | N | N
HOGAN SOUTH | Gresham | HOGAN SOUTH-CLEVELAND | 5324013 | 13 | MULTNOMAH | Y | HOGAN SOUTH WR4 | 28 | 10.1 | 3.6165 | 14.3 | 0.4004 | 0 | N | 9.968% | 3.6165 | 9.968% | N | Y
HOGAN SOUTH | Gresham | HOGAN SOUTH-LAWRENCE | 5324023 | 13 | MULTNOMAH | Y | HOGAN SOUTH WR5 | 28 | 13.1 | 3.7489 | 17.8 | 0.97546 | 0 | N | 20.65% | 3.7489 | 20.65% | N | Y
HOGAN SOUTH | Gresham | HOGAN SOUTH-MAIN | 5324033 | 13 | MULTNOMAH | Y | HOGAN SOUTH WR4 | 28 | 5.7 | 2.2812 | 17.8 | 0.03116 | 0 | N | 1.348% | 2.2812 | 1.348% | N | Y
HOGAN SOUTH | Gresham | HOGAN SOUTH-PAROPA | 5324043 | 13 | MULTNOMAH | Y | HOGAN SOUTH WR5 | 28 | 11.6 | 4.0178 | 14.3 | 0.5477 | 0 | N | 12% | 4.0178 | 12% | N | Y
HOGAN SOUTH | Gresham | HOGAN SOUTH-WALLULA | 5324053 | 13 | MULTNOMAH | Y | HOGAN SOUTH WR4 | 28 | 7.8 | 2.8274 | 14.3 | 0.31027 | 0 | N | 9.889% | 2.8274 | 9.889% | N | Y
HOLGATE | Portland | HOLGATE-BYBEE | 1325043 | 13 | MULTNOMAH | N | HOLGATE BR5 | 22.4 | 9.5 | 4.2 | 13.5 | 0.63774 | 0 | N | 13.18% | 4.2 | 13.18% | N | N
HOLGATE | Portland | HOLGATE-GIDEON | 1325013 | 13 | MULTNOMAH | N | HOLGATE BR4 | 16.8 | 3.9 | 1.925 | 13.5 | 0.134 | 0 | N | 6.508% | 1.925 | 6.508% | N | N
HOLGATE | Portland | HOLGATE-HOLGATE 13 | 1325033 | 13 | MULTNOMAH | N | HOLGATE BR4 | 16.8 | 8.7 | 3.9 | 14.3 | 0.44621 | 0 | N | 10.27% | 3.9 | 10.27% | N | N
HOLGATE | Portland | HOLGATE-KENILWORTH | 1325053 | 13 | MULTNOMAH | N | HOLGATE BR5 | 22.4 | 2.5 | 1.145 | 13.5 | 0.21385 | 0 | N | 15.74% | 1.145 | 15.74% | N | N
HOLGATE | Portland | HOLGATE-RHONE | 1325023 | 13 | MULTNOMAH | N | HOLGATE BR5 | 22.4 | 4.9 | 2.265 | 13.5 | 0.17215 | 0 | N | 7.064% | 2.265 | 7.064% | N | N
HUBER | near Beaverton | HUBER-BANY | 4330053 | 13 | WASHINGTON | Y | HUBER WR1 | 28 | 10.9 | 2.4077 | 17.8 | 0.59465 | 0 | N | 19.81% | 2.4077 | 19.81% | N | N
HUBER | near Beaverton | HUBER-FARMINGTON | 4330023 | 13 | WASHINGTON | Y | HUBER WR2 | 28 | 11.7 | 3.7329 | 14.3 | 0.57515 | 0 | N | 13.35% | 3.7329 | 13.35% | N | N
HUBER | near Beaverton | HUBER-HUBER 13 | 4330013 | 13 | WASHINGTON | Y | HUBER WR2 | 28 | 10 | 3.5913 | 17.8 | 0.38961 | 0 | N | 9.787% | 3.5913 | 9.787% | N | N
HUBER | near Beaverton | HUBER-KINNAMAN | 4330033 | 13 | WASHINGTON | Y | HUBER WR2 | 28 | 7.6 | 2.3728 | 14.3 | 0.58238 | 0 | N | 19.71% | 2.3728 | 19.71% | N | N
HUBER | near Beaverton | HUBER-MARYVILLE | 4330043 | 13 | WASHINGTON | Y | HUBER WR1 | 28 | 13.5 | 3.4299 | 17.8 | 0.7566 | 0 | N | 18.07% | 3.4299 | 18.07% | N | N
INDIAN | near Salem | INDIAN-KEIZER | 2340023 | 13 | MARION | Y | INDIAN WR2 | 28 | 7.6 | 3.1325 | 17.8 | 0.21019 | 0 | N | 6.288% | 3.1325 | 6.288% | N | N
INDIAN | near Salem | INDIAN-LABISH | 2340013 | 13 | MARION | Y | INDIAN WR1 | 28 | 9.7 | 2.8918 | 17.8 | 0.64589 | 0.362 | N | 18.26% | 2.5298 | 28.49% | N | N
INDIAN | near Salem | INDIAN-NORTH | 2340043 | 13 | MARION | Y | INDIAN WR2 | 28 | 12.1 | 0.48697 | 17.8 | 3.4649 | 0 | N | 87.68% | 0.48697 | 87.68% | N | N
INDIAN | near Salem | INDIAN-STATION | 2340033 | 13 | MARION | Y | INDIAN WR2 | 28 | 7.5 | 2.7389 | 18.4 | 0.24212 | 0 | N | 8.122% | 2.7389 | 8.122% | N | N
INDIAN | near Salem | INDIAN-WEST | 2340053 | 13 | MARION | Y | INDIAN WR1 | 28 | 13.1 | 3.8747 | 17.8 | 0.31129 | 0 | N | 7.437% | 3.8747 | 7.437% | N | N
ISLAND | near Milwaukie | ISLAND-13180 | 1345033 | 13 | CLACKAMAS | Y | ISLAND WR1 | 16.8 | 8.384 | 3.9379 | 17.8 | 0.41109 | 0 | N | 9.453% | 3.9379 | 9.453% | N | N
ISLAND | near Milwaukie | ISLAND-13187 | 1345023 | 13 | CLACKAMAS | Y | ISLAND WR2 | 28 | 8.5 | 2.8331 | 17.8 | 0.5952 | 0 | N | 17.36% | 2.8331 | 17.36% | N | N
ISLAND | near Milwaukie | ISLAND-13188 | 1345013 | 13 | CLACKAMAS | Y | ISLAND WR2 | 28 | 10.7 | 4.457 | 17.8 | 0.39432 | 0 | N | 8.128% | 4.457 | 8.128% | N | N
ISLAND | near Milwaukie | ISLAND-ISLAND 13 | 1345043 | 13 | CLACKAMAS | Y | ISLAND WR1 | 16.8 | 3.9 | 1.6913 | 10.4 | 0.01744 | 0 | N | 1.021% | 1.6913 | 1.021% | N | N
JENNINGS LODGE | Jennings Lodge | JENNINGS LODGE-ADDIE | 6365053 | 13 | CLACKAMAS | N | JENNINGS LODGE WR1 | 24.5 | 5.1 | 1.945 | 17.8 | 0.20099 | 0 | N | 9.366% | 1.945 | 9.366% | N | N
JENNINGS LODGE | Jennings Lodge | JENNINGS LODGE-JENNINGS 13 | 6365023 | 13 | CLACKAMAS | N | JENNINGS LODGE WR1 | 24.5 | 9.2 | 3.131 | 14.3 | 0.91561 | 0 | N | 22.63% | 3.131 | 22.63% | N | N
JENNINGS LODGE | Jennings Lodge | JENNINGS LODGE-MELDRUM | 6365033 | 13 | CLACKAMAS | N | JENNINGS LODGE WR1 | 24.5 | 6.9 | 2.7 | 10.7 | 0.23038 | 0 | N | 7.862% | 2.7 | 7.862% | N | N
JENNINGS LODGE | Jennings Lodge | JENNINGS LODGE-OAK GROVE | 6365013 | 13 | CLACKAMAS | N | JENNINGS LODGE WR2 | 28 | 5.1 | 1.78 | 10.7 | 0.23214 | 0 | N | 11.54% | 1.78 | 11.54% | N | N
JENNINGS LODGE | Jennings Lodge | JENNINGS LODGE-WEBSTER | 6365043 | 13 | CLACKAMAS | N | JENNINGS LODGE WR2 | 28 | 7.6 | 2.055 | 14.3 | 0.57313 | 0 | N | 21.81% | 2.055 | 21.81% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 0 | 0 | 20.9 | 0 | 0 | N | 0% | 0 | 0% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 0 | 0 | 20.9 | 0 | 0 | N | 0% | 0 | 0% | N | N
KELLEY POINT | Portland | KELLEY POINT-KELLEY POINT 13 | 1367013 | 13 | MULTNOMAH | Y | KELLEY POINT WR1 | 28 | 2.8 | 0.30556 | 18.4 | 0 | 0 | N | 0% | 0.30556 | 0% | N | N
KELLEY POINT | Portland | KELLEY POINT-LEDBETTER | 1367043 | 13 | MULTNOMAH | Y | KELLEY POINT WR1 | 28 | 3 | 0.84122 | 18.4 | 0 | 0 | N | 0% | 0.84122 | 0% | N | N
KELLEY POINT | Portland | KELLEY POINT-MARINE | 1367023 | 13 | MULTNOMAH | Y | KELLEY POINT WR2 | 28 | 6.1 | 1.4819 | 18.4 | 0 | 0 | N | 0% | 1.4819 | 0% | N | N
KELLEY POINT | Portland | KELLEY POINT-SIMMONS | 1367033 | 13 | MULTNOMAH | Y | KELLEY POINT WR2 | 28 | 2.4 | 0.75328 | 18.4 | 0 | 0 | N | 0% | 0.75328 | 0% | N | N
KELLY BUTTE | Portland | KELLY BUTTE-BINNSMEAD | 1370023 | 13 | MULTNOMAH | Y | KELLY BUTTE WR1 | 22.4 | 10.6 | 4.5541 | 17.8 | 0.36946 | 0 | N | 7.504% | 4.5541 | 7.504% | N | N
KELLY BUTTE | Portland | KELLY BUTTE-FAIRLAWN | 1370033 | 13 | MULTNOMAH | Y | KELLY BUTTE WR2 | 22.4 | 5.7 | 2.8293 | 17.8 | 0.066425 | 0 | N | 2.294% | 2.8293 | 2.294% | N | N
KELLY BUTTE | Portland | KELLY BUTTE-MALL 205 | 1370043 | 13 | MULTNOMAH | Y | KELLY BUTTE WR1 | 22.4 | 12.6 | 5.2024 | 17.8 | 0.64471 | 0 | N | 11.03% | 5.2024 | 11.03% | N | N
KELLY BUTTE | Portland | KELLY BUTTE-MCGREW | 1370013 | 13 | MULTNOMAH | Y | KELLY BUTTE WR2 | 22.4 | 8.5 | 3.5037 | 17.8 | 0.31258 | 0 | N | 8.191% | 3.5037 | 8.191% | N | N
KING CITY | near King City | KING CITY-BULL MOUNTAIN | 4378023 | 13 | WASHINGTON | Y | KING CITY WR1 | 28 | 4.2 | 1.264 | 17.8 | 0.17818 | 0 | N | 12.35% | 1.264 | 12.35% | Y | Y
KING CITY | near King City | KING CITY-FISCHER | 4378013 | 13 | WASHINGTON | Y | KING CITY WR1 | 28 | 9.8 | 2.1739 | 17.8 | 0.60325 | 0 | N | 21.72% | 2.1739 | 21.72% | Y | Y
KING CITY | near King City | KING CITY-HAZELBROOK | 4378043 | 13 | WASHINGTON | Y | KING CITY WR2 | 28 | 8.5 | 2.7397 | 17.8 | 0.25033 | 0 | N | 8.372% | 2.7397 | 8.372% | Y | Y
KING CITY | near King City | KING CITY-NORTH | 4378053 | 13 | WASHINGTON | Y | KING CITY WR2 | 28 | 6.3 | 2.2829 | 14.3 | 0.33869 | 0 | N | 12.92% | 2.2829 | 12.92% | Y | Y
KING CITY | near King City | KING CITY-SUMMERFIELD | 4378033 | 13 | WASHINGTON | Y | KING CITY WR2 | 28 | 7.5 | 2.319 | 14.3 | 0.18621 | 0 | N | 7.433% | 2.319 | 7.433% | Y | Y
LELAND | Oregon City | LELAND-BEAVERCREEK | 6402013 | 13 | CLACKAMAS | Y | LELAND BR1 | 28 | 12 | 5.4247 | 17.8 | 0.99141 | 1.991 | N | 15.45% | 3.4337 | 46.48% | N | Y
LELAND | Oregon City | LELAND-CARUS | 6402023 | 13 | CLACKAMAS | Y | LELAND BR1 | 28 | 9.351 | 3.9949 | 17.8 | 0.5525 | 2.5 | N | 12.15% | 1.4949 | 67.13% | N | Y
LELAND | Oregon City | LELAND-KELM | 6402033 | 13 | CLACKAMAS | Y | LELAND BR1 | 28 | 7.8 | 2.5682 | 17.8 | 0.58821 | 0 | N | 18.64% | 2.5682 | 18.64% | N | Y
LENTS | near Portland | LENTS-13101 | 1405013 | 13 | MULTNOMAH | Y | LENTS WR3 | 22.4 | 6.3 | 2.3512 | 17.8 | 0.19723 | 0 | N | 7.739% | 2.3512 | 7.739% | N | Y
LENTS | near Portland | LENTS-HAPPY VALLEY | 1405043 | 13 | MULTNOMAH | Y | LENTS WR3 | 22.4 | 12.2 | 4.5223 | 17.8 | 0.36914 | 0 | N | 7.547% | 4.5223 | 7.547% | N | Y
LENTS | near Portland | LENTS-MT SCOTT | 1405023 | 13 | MULTNOMAH | Y | LENTS RK2 | 10 | 0.7 | 0.086959 | 13.7 | 0.01059 | 0 | N | 10.86% | 0.086959 | 10.86% | N | Y
LENTS | near Portland | LENTS-NORTH | 1405033 | 13 | MULTNOMAH | Y | LENTS RK2 | 10 | 4.4 | 1.6494 | 10.4 | 0.28931 | 0 | N | 14.92% | 1.6494 | 14.92% | N | Y
LIBERAL | Molalla | LIBERAL-LIBERAL 13 | 6464013 | 13 | CLACKAMAS | Y | LIBERAL BR1 | 8.4 | 5 | -2.2674 | 13.5 | 4.546 | 0 | Y | 199.5% | -2.2674 | 199.5% | Y | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 8.4 | 6.2283 | 0.83403 | 17.8 | 0 | 0 | Y | 0% | 0.83403 | 0% | N | N
LIBERTY | Salem | LIBERTY-BROWNING | 2410013 | 13 | MARION | Y | LIBERTY WR1 | 22.4 | 2.1 | 0.5052 | 7.8 | 0.072055 | 0 | N | 12.48% | 0.5052 | 12.48% | N | N
LIBERTY | Salem | LIBERTY-LONE OAK | 2410043 | 13 | MARION | Y | LIBERTY WR2 | 28 | 8.3 | 2.232 | 17.8 | 0.44681 | 0 | N | 16.68% | 2.232 | 16.68% | N | N
LIBERTY | Salem | LIBERTY-MORNINGSIDE | 2410053 | 13 | MARION | Y | LIBERTY WR2 | 28 | 8.4 | 3.1963 | 14.3 | 0.26613 | 0 | N | 7.686% | 3.1963 | 7.686% | N | N
LIBERTY | Salem | LIBERTY-ROSEDALE | 2410023 | 13 | MARION | Y | LIBERTY WR1 | 22.4 | 9.2 | 2.5316 | 17.8 | 0.90588 | 0 | N | 26.35% | 2.5316 | 26.35% | N | N
LIBERTY | Salem | LIBERTY-SKYLINE | 2410063 | 13 | MARION | Y | LIBERTY WR2 | 28 | 11.2 | 4.3106 | 17.8 | 0.82898 | 0 | N | 16.13% | 4.3106 | 16.13% | N | N
LIBERTY | Salem | LIBERTY-VISTA | 2410033 | 13 | MARION | Y | LIBERTY WR1 | 22.4 | 5.5 | 1.9802 | 14.3 | 0.15709 | 0 | N | 7.35% | 1.9802 | 7.35% | N | N
MAIN | Hillsboro | MAIN-AIRPORT | 4422023 | 13 | WASHINGTON | Y | MAIN BR1 | 28 | 6.29 | 2.1704 | 17.8 | 0.48132 | 0 | N | 18.15% | 2.1704 | 18.15% | N | N
MAIN | Hillsboro | MAIN-BENTLEY | 4422033 | 13 | WASHINGTON | Y | MAIN BR1 | 28 | 7.1 | 1.6788 | 17.8 | 0.91213 | 0 | N | 35.2% | 1.6788 | 35.2% | N | N
MAIN | Hillsboro | MAIN-EXPRESS | 4422053 | 13 | WASHINGTON | Y | MAIN BR1 | 28 | 10.55 | 4.3989 | 17.8 | 0.27294 | 0 | N | 5.842% | 4.3989 | 5.842% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 1.47 | 0.98483 | 17.8 | 0 | 0 | N | 0% | 0.98483 | 0% | N | N
MAIN | Hillsboro | MAIN-RIVER | 4422013 | 13 | WASHINGTON | Y | MAIN BR2 | 28 | 10.65 | 3.5664 | 17.8 | 0.70314 | 0 | N | 16.47% | 3.5664 | 16.47% | N | N
MARKET | Salem | MARKET-ENGLEWOOD | 2425013 | 13 | MARION | Y | MARKET WR1 | 28 | 7.1 | 1.472 | 17.8 | 0.14513 | 0 | N | 8.975% | 1.472 | 8.975% | N | Y
MARKET | Salem | MARKET-FAIRGROUNDS | 2425033 | 13 | MARION | Y | MARKET WR1 | 28 | 6 | 2.815 | 11 | 0.19477 | 0 | N | 6.471% | 2.815 | 6.471% | N | Y
MARKET | Salem | MARKET-HAWTHORNE | 2425023 | 13 | MARION | Y | MARKET WR1 | 28 | 7.7 | 3.0025 | 17.8 | 0.10147 | 0 | N | 3.269% | 3.0025 | 3.269% | N | Y
MARKET | Salem | MARKET-PARK | 2425043 | 13 | MARION | Y | MARKET WR1 | 28 | 5 | 2.0726 | 17.8 | 0.10891 | 0 | N | 4.993% | 2.0726 | 4.993% | Y | Y
MARQUAM | Portland | MARQUAM-GROVER | 1430323 | 13 | MULTNOMAH | Y | MARQUAM WR4 | 50 | 0 | 0 | 17.8 | 0 | 0 | N | 0% | 0 | 0% | Y | Y
MARQUAM | Portland | MARQUAM-LILAC | 1430273 | 13 | MULTNOMAH | Y | MARQUAM WR5 | 50 | 0 | 0 | 17.8 | 0 | 0 | N | 0% | 0 | 0% | Y | Y
MARQUAM | Portland | MARQUAM-MCCALL #10 NETWORK | 1430133 | 13 | MULTNOMAH | Y | MARQUAM WR2 | 50 | 2.8 | 0.89418 | 5.5 | 0.02336 | 0 | Y | 2.546% | 0.89418 | 2.546% | Y | Y
MARQUAM | Portland | MARQUAM-MCCALL #11 NETWORK | 1430083 | 13 | MULTNOMAH | Y | MARQUAM WR1-2-3 | 50 | 1.5 | 0.82429 | 5.5 | 0.00676 | 0 | Y | 0.8134% | 0.82429 | 0.8134% | Y | Y
MARQUAM | Portland | MARQUAM-MCCALL #12 NETWORK | 1430033 | 13 | MULTNOMAH | Y | MARQUAM WR3 | 50 | 2.4 | 0.82248 | 5.5 | 0 | 0 | Y | 0% | 0.82248 | 0% | Y | Y
MARQUAM | Portland | MARQUAM-MCCALL #9 NETWORK | 1430183 | 13 | MULTNOMAH | Y | MARQUAM WR1 | 50 | 2.3 | 0.7 | 5.5 | 0.03024 | 0 | Y | 4.141% | 0.7 | 4.141% | Y | Y
MARQUAM | Portland | MARQUAM-MEADE | 1430213 | 13 | MULTNOMAH | Y | MARQUAM WR4 | 50 | 6 | 2.9694 | 0 | 0.089602 | 0 | N | 2.929% | 2.9694 | 2.929% | Y | Y
MARQUAM | Portland | MARQUAM-ORANGE | 1430253 | 13 | MULTNOMAH | Y | MARQUAM WR4 | 50 | 4.4 | 2.3678 | 18.3 | 0.0198 | 0 | N | 0.8293% | 2.3678 | 0.8293% | Y | Y
MARQUAM | Portland | MARQUAM-PORTER | 1430263 | 13 | MULTNOMAH | Y | MARQUAM WR5 | 50 | 3.3 | 1.3501 | 0 | 0 | 0 | N | 0% | 1.3501 | 0% | Y | Y
MARQUAM | Portland | MARQUAM-SPIRIT #1 NETWORK | 1430163 | 13 | MULTNOMAH | Y | MARQUAM WR1 | 50 | 2 | 0.6497 | 5.5 | 0 | 0 | Y | 0% | 0.6497 | 0% | Y | Y
MARQUAM | Portland | MARQUAM-SPIRIT #2 NETWORK | 1430113 | 13 | MULTNOMAH | Y | MARQUAM WR2 | 50 | 2.2 | 0.70056 | 5.5 | 0 | 0 | Y | 0% | 0.70056 | 0% | Y | Y
MARQUAM | Portland | MARQUAM-SPIRIT #3 NETWORK | 1430063 | 13 | MULTNOMAH | Y | MARQUAM WR1-2-3 | 50 | 2.3 | 0.74952 | 5.5 | 0 | 0 | Y | 0% | 0.74952 | 0% | Y | Y
MARQUAM | Portland | MARQUAM-SPIRIT #4 NETWORK | 1430013 | 13 | MULTNOMAH | Y | MARQUAM WR3 | 50 | 2.2 | 0.7259 | 5.5 | 0 | 0 | Y | 0% | 0.7259 | 0% | Y | Y
MARQUAM | Portland | MARQUAM-TILIKUM | 1430303 | 13 | MULTNOMAH | Y | MARQUAM WR5 | 50 | 5.2 | 2.3996 | 18.3 | 0 | 0 | N | 0% | 2.3996 | 0% | Y | Y
MCCLAIN | Salem | MCCLAIN-COTTAGE | 2435033 | 13 | MARION | Y | MCCLAIN BR1 | 7.5 | 4.4 | 1.6571 | 8.3 | 0.08251 | 0 | N | 4.743% | 1.6571 | 4.743% | N | N
MCCLAIN | Salem | MCCLAIN-FRONT | 2435013 | 13 | MARION | Y | MCCLAIN BR3 | 7.5 | 4.6 | 1.712 | 9.9 | 0.12505 | 0 | N | 6.807% | 1.712 | 6.807% | N | N
MCCLAIN | Salem | MCCLAIN-HOLLYWOOD | 2435043 | 13 | MARION | Y | MCCLAIN BR2 | 7.5 | 3.9 | 1.6576 | 8.3 | 0.44084 | 0 | N | 21.01% | 1.6576 | 21.01% | N | N
MCGILL | Gresham | MCGILL-HORSETAIL | 5440123 | 13 | MULTNOMAH | Y | MCGILL WR3 | 28 | 7.4 | 2.6678 | 14.3 | 0.34018 | 0 | N | 11.31% | 2.6678 | 11.31% | Y | Y
MCGILL | Gresham | MCGILL-LATOURELL | 5440113 | 13 | MULTNOMAH | Y | MCGILL WR3 | 28 | 8.1 | 2.518 | 14.3 | 0.31859 | 0 | N | 11.23% | 2.518 | 11.23% | Y | Y
MCGILL | Gresham | MCGILL-TOKETEE | 5440133 | 13 | MULTNOMAH | Y | MCGILL WR3 | 28 | 5.4 | 3.4754 | 18.4 | 0 | 0 | N | 0% | 3.4754 | 0% | Y | Y
MERIDIAN | near Tualatin | MERIDIAN-65TH | 4447083 | 13 | CLACKAMAS | Y | MERIDIAN WR2 | 28 | 4.2 | 1.7899 | 14.3 | 0 | 0 | N | 0% | 1.7899 | 0% | N | Y
MERIDIAN | near Tualatin | MERIDIAN-BORLAND | 4447053 | 13 | CLACKAMAS | Y | MERIDIAN WR2 | 28 | 6.4 | 2.0695 | 17.8 | 0.24477 | 0 | N | 10.58% | 2.0695 | 10.58% | N | Y
MERIDIAN | near Tualatin | MERIDIAN-CHILDS | 4447093 | 13 | CLACKAMAS | Y | MERIDIAN WR3 | 28 | 6.2 | 2.4976 | 14.3 | 0.26977 | 0 | N | 9.748% | 2.4976 | 9.748% | N | Y
MERIDIAN | near Tualatin | MERIDIAN-LAKEVIEW | 4447063 | 13 | CLACKAMAS | Y | MERIDIAN WR1 | 28 | 5 | 1.8561 | 17.8 | 0.12485 | 0 | N | 6.303% | 1.8561 | 6.303% | N | Y
MERIDIAN | near Tualatin | MERIDIAN-MERIDIAN 13 | 4447013 | 13 | CLACKAMAS | Y | MERIDIAN WR1 | 28 | 6.5 | 1.8901 | 14.3 | 0.45293 | 0 | N | 19.33% | 1.8901 | 19.33% | N | Y
MERIDIAN | near Tualatin | MERIDIAN-NYBERG | 4447073 | 13 | CLACKAMAS | Y | MERIDIAN WR3 | 28 | 3.6 | 1.1575 | 17.8 | 0 | 0 | N | 0% | 1.1575 | 0% | N | Y
MERIDIAN | near Tualatin | MERIDIAN-PILKINGTON | 4447043 | 13 | CLACKAMAS | Y | MERIDIAN WR2 | 28 | 8.7 | 2.7433 | 17.8 | 0.40768 | 0 | N | 12.94% | 2.7433 | 12.94% | N | Y
MERIDIAN | near Tualatin | MERIDIAN-SAGERT | 4447033 | 13 | CLACKAMAS | Y | MERIDIAN WR1 | 28 | 8.5 | 3.4994 | 17.8 | 0.21061 | 0 | N | 5.677% | 3.4994 | 5.677% | N | Y
MIDDLE GROVE | near Middle Grove | MIDDLE GROVE-BROWN | 2450023 | 13 | MARION | Y | MIDDLE GROVE WR1 | 22.4 | 7.9 | 3.122 | 17.8 | 0.43872 | 0 | N | 12.32% | 3.122 | 12.32% | N | N
MIDDLE GROVE | near Middle Grove | MIDDLE GROVE-CHEMEKETA | 2450043 | 13 | MARION | Y | MIDDLE GROVE WR2 | 28 | 5.9 | 1.132 | 10.4 | 0.50513 | 0 | N | 30.85% | 1.132 | 30.85% | N | N
MIDDLE GROVE | near Middle Grove | MIDDLE GROVE-CORDON | 2450033 | 13 | MARION | Y | MIDDLE GROVE WR2 | 28 | 12.1 | 0.31674 | 17.8 | 5.1966 | 0 | N | 94.26% | 0.31674 | 94.26% | Y | N
MIDDLE GROVE | near Middle Grove | MIDDLE GROVE-SWEGLE | 2450013 | 13 | MARION | Y | MIDDLE GROVE WR1 | 22.4 | 9 | 3.8573 | 14.3 | 0.32069 | 0 | N | 7.676% | 3.8573 | 7.676% | N | N
MIDDLE GROVE | near Middle Grove | MIDDLE GROVE-WEST | 2450053 | 13 | MARION | Y | MIDDLE GROVE WR2 | 28 | 10 | 4.2309 | 17.8 | 0.14297 | 0 | N | 3.269% | 4.2309 | 3.269% | N | N
MIDWAY | near Portland | MIDWAY-DIVISION | 5455013 | 13 | MULTNOMAH | N | MIDWAY WR1 | 16.8 | 6.8 | 3.015 | 17.8 | 0.17246 | 0 | N | 5.411% | 3.015 | 5.411% | N | N
MIDWAY | near Portland | MIDWAY-DOUGLAS | 5455023 | 13 | MULTNOMAH | N | MIDWAY WR1 | 16.8 | 6.1 | 2.42 | 17.8 | 0.15966 | 0 | N | 6.189% | 2.42 | 6.189% | N | N
MIDWAY | near Portland | MIDWAY-LYNCH | 5455033 | 13 | MULTNOMAH | N | MIDWAY WR2 | 16.8 | 6 | 2.1 | 17.8 | 0.16817 | 0 | N | 7.414% | 2.1 | 7.414% | N | N
MIDWAY | near Portland | MIDWAY-POWELLHURST | 5455043 | 13 | MULTNOMAH | N | MIDWAY WR2 | 16.8 | 7.5 | 3.235 | 10.4 | 0.09128 | 0 | N | 2.744% | 3.235 | 2.744% | N | N
MILL CREEK | near Salem | MILL CREEK-EASTLAND | 2540013 | 13 | MARION | Y | MILL CREEK WR1 | 16.8 | 5 | 0.54166 | 10.7 | 1.8206 | 0 | N | 77.07% | 0.54166 | 77.07% | N | Y
MILL CREEK | near Salem | MILL CREEK-KUEBLER | 2540023 | 13 | MARION | Y | MILL CREEK WR1 | 16.8 | 5.3 | 1.9917 | 17.8 | 0.27377 | 0 | N | 12.08% | 1.9917 | 12.08% | N | Y
MILL CREEK | near Salem | MILL CREEK-MILL CREEK 13 | 2540033 | 13 | MARION | Y | MILL CREEK WR1 | 16.8 | 4.7 | 1.9745 | 17.8 | 0.03518 | 0 | N | 1.751% | 1.9745 | 1.751% | N | Y
MOLALLA | Molalla | MOLALLA-BUCKAROO | 6466023 | 13 | CLACKAMAS | Y | MOLALLA BR2 | 20 | 10.5287 | 3.6758 | 14.3 | 0.62784 | 0 | N | 14.59% | 3.6758 | 14.59% | N | Y
MOLALLA | Molalla | MOLALLA-FOREST | 6466043 | 13 | CLACKAMAS | Y | MOLALLA BR1 | 22.4 | 8.2887 | 2.8751 | 17.8 | 0.36482 | 1.265 | N | 11.26% | 1.6101 | 50.3% | N | Y
MOLALLA | Molalla | MOLALLA-MARQUAM | 6466013 | 13 | CLACKAMAS | Y | MOLALLA BR2 | 20 | 4.2782 | -4.2053 | 7.3 | 7.1299 | 7.22 | N | 243.8% | -11.4253 | 490.7% | Y | Y
MOLALLA | Molalla | MOLALLA-YODER | 6466033 | 13 | CLACKAMAS | Y | MOLALLA BR1 | 22.4 | 9.7124 | 0.93713 | 14.3 | 3.8293 | 0 | N | 80.34% | 0.93713 | 80.34% | Y | Y
MT ANGEL | Mt. Angel | MT ANGEL-EAST | 2470013 | 13 | MARION | Y | MT ANGEL BR1 | 20 | 3.2 | 1.1693 | 10.7 | 0.081965 | 0 | N | 6.551% | 1.1693 | 6.551% | N | Y
MT ANGEL | Mt. Angel | MT ANGEL-WEST | 2470023 | 13 | MARION | Y | MT ANGEL BR1 | 20 | 7.5 | 0.33356 | 10.4 | 3.351 | 2.97 | N | 90.95% | -2.6364 | 171.6% | Y | Y
MT PLEASANT | Oregon City | MT PLEASANT-CLAIRMONT | 6475023 | 13 | CLACKAMAS | N | MT PLEASANT WR1 | 28 | 13.251 | 4.205 | 17.8 | 1.1442 | 0 | N | 21.39% | 4.205 | 21.39% | N | N
MT PLEASANT | Oregon City | MT PLEASANT-MT VIEW | 6475043 | 13 | CLACKAMAS | N | MT PLEASANT WR1 | 28 | 10.765 | 4.68 | 17.8 | 0.2814 | 0 | N | 5.672% | 4.68 | 5.672% | N | N
MT PLEASANT | Oregon City | MT PLEASANT-RIVERCREST | 6475053 | 13 | CLACKAMAS | N | MT PLEASANT WR2 | 16.8 | 3.3 | 1.17 | 17.8 | 0.21839 | 0 | N | 15.73% | 1.17 | 15.73% | N | N
MT PLEASANT | Oregon City | MT PLEASANT-SOUTH END | 6475033 | 13 | CLACKAMAS | N | MT PLEASANT WR2 | 16.8 | 12.4 | 2.875 | 17.8 | 1.1772 | 0 | N | 29.05% | 2.875 | 29.05% | N | N
MULINO | Mulino | MULINO-NORTH | 6478013 | 13 | CLACKAMAS | N | MULINO BR1 | 7.5 | 1.6 | 0.77085 | 8.8 | 0.06366 | 0 | N | 7.628% | 0.77085 | 7.628% | N | N
MULINO | Mulino | MULINO-SOUTH | 6478023 | 13 | CLACKAMAS | N | MULINO BR1 | 7.5 | 3.4 | 1.53 | 8.8 | 0.22767 | 0 | N | 12.95% | 1.53 | 12.95% | N | N
MULTNOMAH | Portland | MULTNOMAH-13176 | 1480023 | 13 | MULTNOMAH | N | MULTNOMAH WR2 | 16.8 | 8.1 | 2.9999 | 17.8 | 0.38109 | 0 | N | 11.27% | 2.9999 | 11.27% | N | N
MULTNOMAH | Portland | MULTNOMAH-13177 | 1480033 | 13 | MULTNOMAH | N | MULTNOMAH WR1 | 22.4 | 8 | 3.405 | 17.8 | 0.26796 | 0 | N | 7.295% | 3.405 | 7.295% | N | N
MULTNOMAH | Portland | MULTNOMAH-13181 | 1480013 | 13 | MULTNOMAH | N | MULTNOMAH WR2 | 16.8 | 5.9 | 1.935 | 17.8 | 0.33073 | 0 | N | 14.6% | 1.935 | 14.6% | N | N
MULTNOMAH | Portland | MULTNOMAH-MULTNOMAH 13 | 1480063 | 13 | MULTNOMAH | N | MULTNOMAH WR1 | 22.4 | 6.6 | 1.983 | 17.8 | 0.40838 | 0 | N | 17.08% | 1.983 | 17.08% | N | N
MURRAYHILL | Beaverton | MURRAYHILL-KINTON | 4482033 | 13 | WASHINGTON | Y | MURRAYHILL WR2 | 28 | 15.4 | 4.0864 | 17.8 | 0.8987 | 0 | N | 18.03% | 4.0864 | 18.03% | N | N
MURRAYHILL | Beaverton | MURRAYHILL-MURRAYHILL 13 | 4482013 | 13 | WASHINGTON | Y | MURRAYHILL WR1 | 28 | 8.7 | 3.8725 | 17.8 | 0.5156 | 0 | N | 11.75% | 3.8725 | 11.75% | N | N
MURRAYHILL | Beaverton | MURRAYHILL-REUSSER | 4482043 | 13 | WASHINGTON | Y | MURRAYHILL WR2 | 28 | 7.8 | 1.7404 | 18.4 | 0.31379 | 0 | N | 15.28% | 1.7404 | 15.28% | N | N
MURRAYHILL | Beaverton | MURRAYHILL-TEAL | 4482023 | 13 | WASHINGTON | Y | MURRAYHILL WR1 | 28 | 12.2 | 3.5216 | 18.4 | 0.73298 | 0 | N | 17.23% | 3.5216 | 17.23% | N | N
NEWBERG | Newberg | NEWBERG-CHEHALEM | 4485033 | 13 | YAMHILL | Y | NEWBERG WR1 | 22.4 | 11.6623 | 3.8175 | 17.8 | 1.086 | 0 | N | 22.15% | 3.8175 | 22.15% | N | Y
NEWBERG | Newberg | NEWBERG-DUNDEE | 4485023 | 13 | YAMHILL | Y | NEWBERG WR1 | 22.4 | 11.0586 | 4.1072 | 17.8 | 1.0486 | 2.5 | N | 20.34% | 1.6072 | 68.83% | N | Y
NEWBERG | Newberg | NEWBERG-HOOVER PARK | 4485053 | 13 | YAMHILL | Y | NEWBERG WR2 | 22.4 | 10.7503 | 3.7939 | 17.8 | 0.46542 | 0 | N | 10.93% | 3.7939 | 10.93% | N | Y
NEWBERG | Newberg | NEWBERG-NORTH COLLEGE | 4485043 | 13 | YAMHILL | Y | NEWBERG WR2 | 22.4 | 8.8663 | 2.5286 | 17.8 | 1.1306 | 0 | N | 30.9% | 2.5286 | 30.9% | N | Y
NORTH MARION | near Woodburn | NORTH MARION-CROSBY | 2505043 | 13 | MARION | Y | NORTH MARION BR1 | 14 | 9.6 | 2.6499 | 17.8 | 0.48936 | 0 | N | 15.59% | 2.6499 | 15.59% | N | N
NORTH MARION | near Woodburn | NORTH MARION-FRONT | 2505033 | 13 | MARION | Y | NORTH MARION BR2 | 7.5 | 5.3766 | 1.4995 | 10.7 | 0.3043 | 0 | N | 16.87% | 1.4995 | 16.87% | N | N
NORTH MARION | near Woodburn | NORTH MARION-HUBBARD | 2505013 | 13 | MARION | Y | NORTH MARION BR1 | 14 | 6.0495 | 1.8131 | 17.8 | 0.55766 | 0 | N | 23.52% | 1.8131 | 23.52% | N | N
NORTH MARION | near Woodburn | NORTH MARION-MCLAREN | 2505023 | 13 | MARION | Y | NORTH MARION BR3 | 9.4 | 6.3097 | 1.9495 | 17.8 | 0.14173 | 0 | N | 6.777% | 1.9495 | 6.777% | N | N
NORTH PLAINS | NorthPlains | NORTH PLAINS-MASON HILL | 4510023 | 13 | WASHINGTON | Y | NORTH PLAINS BR1 | 20 | 8.73 | 3.1305 | 10.4 | 1.2535 | 0 | N | 28.59% | 3.1305 | 28.59% | N | N
NORTH PLAINS | NorthPlains | NORTH PLAINS-NORTH PLAINS 13 | 4510013 | 13 | WASHINGTON | Y | NORTH PLAINS BR1 | 20 | 5.23 | 1.6401 | 10.4 | 0.49024 | 0 | N | 23.01% | 1.6401 | 23.01% | N | N
NORTHERN | Portland | NORTHERN-11009 | 1495143 | 13 | MULTNOMAH | Y | NORTHERN WR1 | 28 | 4.5 | 1.9118 | 12.2 | 0.49827 | 0 | N | 20.67% | 1.9118 | 20.67% | Y | Y
NORTHERN | Portland | NORTHERN-11016 | 1493163 | 13 | MULTNOMAH | Y | NORTHERN WR1 | 28 | 1 | 0.30479 | 7.6 | 0.03486 | 0 | N | 10.26% | 0.30479 | 10.26% | Y | Y
NORTHERN | Portland | NORTHERN-11071 | 1495153 | 13 | MULTNOMAH | Y | NORTHERN WR1 | 28 | 5.3 | 2.0521 | 9.4 | 0.17101 | 0 | N | 7.692% | 2.0521 | 7.692% | Y | Y
OAK GROVE | Oak Grove | OAK GROVE-LAKE HARRIET | 5515013 | 13 | CLACKAMAS | Y | OAK GROVE WR9 | 8.4 | 0.4 | 0.11488 | 7.8 | 0.133 | 0 | N | 53.66% | 0.11488 | 53.66% | N | N
OAK GROVE | Oak Grove | OAK GROVE-WHITE WATER | 5515023 | 13 | CLACKAMAS | Y | OAK GROVE WR9 | 8.4 | 0 | 0 | 7.8 | 0 | 0 | N | 0% | 0 | 0% | N | N
OAK HILLS | near Beaverton | OAK HILLS-FIVE OAKS | 4516033 | 13 | WASHINGTON | Y | OAK HILLS WR1 | 22.4 | 12.7 | 5.5984 | 17.8 | 0.21991 | 0 | N | 3.78% | 5.5984 | 3.78% | N | N
OAK HILLS | near Beaverton | OAK HILLS-GREENBRIER | 4516053 | 13 | WASHINGTON | Y | OAK HILLS WR2 | 22.4 | 9.9 | 3.542 | 17.8 | 0.16706 | 0 | N | 4.504% | 3.542 | 4.504% | N | N
OAK HILLS | near Beaverton | OAK HILLS-OAK HILLS 13 | 4516013 | 13 | WASHINGTON | Y | OAK HILLS WR1 | 22.4 | 6.6 | 1.6212 | 17.8 | 0.40347 | 0.724 | N | 19.93% | 0.89721 | 55.69% | N | N
OAK HILLS | near Beaverton | OAK HILLS-SOMERSET | 4516023 | 13 | WASHINGTON | Y | OAK HILLS WR2 | 22.4 | 4.5 | 1.0949 | 17.8 | 0.26908 | 0 | N | 19.73% | 1.0949 | 19.73% | N | N
OAK HILLS | near Beaverton | OAK HILLS-WALKER | 4516043 | 13 | WASHINGTON | Y | OAK HILLS WR2 | 22.4 | 7.6 | 2.4668 | 17.8 | 0.78862 | 0 | N | 24.22% | 2.4668 | 24.22% | N | N
ORENCO | near Hillsboro | ORENCO-231ST | 4518433 | 13 | WASHINGTON | Y | ORENCO WR4 | 28 | 6.91 | 3.6245 | 17.8 | 0.05309 | 0 | N | 1.444% | 3.6245 | 1.444% | N | N
ORENCO | near Hillsboro | ORENCO-AMBERGLEN | 4518543 | 13 | WASHINGTON | Y | ORENCO WR5 | 28 | 8.98 | 3.616 | 17.8 | 0.13461 | 0 | N | 3.589% | 3.616 | 3.589% | N | N
ORENCO | near Hillsboro | ORENCO-BASELINE | 4518523 | 13 | WASHINGTON | Y | ORENCO WR5 | 28 | 9.46 | 2.8013 | 17.8 | 1.663 | 0 | N | 37.25% | 2.8013 | 37.25% | N | N
ORENCO | near Hillsboro | ORENCO-ORENCO 13 | 4518313 | 13 | WASHINGTON | Y | ORENCO WR3 | 28 | 5.98 | 2.2596 | 17.8 | 0.24269 | 0 | N | 9.699% | 2.2596 | 9.699% | N | N
ORENCO | near Hillsboro | ORENCO-PRIMATE | 4518323 | 13 | WASHINGTON | Y | ORENCO WR3 | 28 | 10.65 | 4.6069 | 17.8 | 0.31485 | 0 | N | 6.397% | 4.6069 | 6.397% | N | N
ORENCO | near Hillsboro | ORENCO-WILKINS | 4518443 | 13 | WASHINGTON | Y | ORENCO WR4 | 28 | 11.25 | 5.2627 | 18.4 | 0.13997 | 0 | N | 2.591% | 5.2627 | 2.591% | N | N
ORIENT | near Gresham | ORIENT-BARLOW | 5517023 | 13 | MULTNOMAH | Y | ORIENT BR1 | 28 | 7.6 | 2.8006 | 10.4 | 0.26136 | 0 | N | 8.536% | 2.8006 | 8.536% | Y | Y
ORIENT | near Gresham | ORIENT-ORIENT 13 | 5517013 | 13 | MULTNOMAH | Y | ORIENT BR1 | 28 | 5.6 | 1.7149 | 10.4 | 0.60978 | 0 | N | 26.23% | 1.7149 | 26.23% | Y | Y
ORIENT | near Gresham | ORIENT-OXBOW | 5517033 | 13 | MULTNOMAH | Y | ORIENT BR1 | 28 | 2.7 | 1.2262 | 10.4 | 0.17506 | 0 | N | 12.49% | 1.2262 | 12.49% | Y | Y
OSWEGO | Lake Oswego | OSWEGO-IRON MOUNTAIN | 1520013 | 13 | CLACKAMAS | Y | OSWEGO WR3 | 16.8 | 6.8 | 2.3315 | 9.9 | 0.073805 | 0 | N | 3.068% | 2.3315 | 3.068% | N | Y
OSWEGO | Lake Oswego | OSWEGO-MARYLHURST | 1520033 | 13 | CLACKAMAS | Y | OSWEGO WR1 | 16.8 | 10.1 | 3.5947 | 17.8 | 0.40258 | 0 | N | 10.07% | 3.5947 | 10.07% | N | Y
OSWEGO | Lake Oswego | OSWEGO-PALATINE | 1520043 | 13 | CLACKAMAS | Y | OSWEGO WR1 | 16.8 | 6.7 | 2.5543 | 17.8 | 0.18393 | 0 | N | 6.717% | 2.5543 | 6.717% | N | Y
OSWEGO | Lake Oswego | OSWEGO-STAFFORD | 1520023 | 13 | CLACKAMAS | Y | OSWEGO WR3 | 16.8 | 5.9 | 2.0293 | 17.8 | 0.10559 | 0 | N | 4.946% | 2.0293 | 4.946% | N | Y
OXFORD | Salem | OXFORD-FAIRVIEW | 2523013 | 13 | MARION | Y | OXFORD WR2 | 28 | 8.7 | 4.3533 | 17.8 | 0.4514 | 0 | N | 9.395% | 4.3533 | 9.395% | N | N
OXFORD | Salem | OXFORD-LEE | 2523063 | 13 | MARION | Y | OXFORD WR1 | 22.4 | 7.6 | 2.8534 | 17.8 | 0.05852 | 0 | N | 2.01% | 2.8534 | 2.01% | N | N
OXFORD | Salem | OXFORD-MADRONA | 2523033 | 13 | MARION | Y | OXFORD WR2 | 28 | 3.7 | 1.2235 | 13.5 | 0.01595 | 0 | N | 1.287% | 1.2235 | 1.287% | N | N
OXFORD | Salem | OXFORD-OXFORD 13 | 2523043 | 13 | MARION | Y | OXFORD WR2 | 28 | 3.4 | 1.1236 | 17.8 | 0.32451 | 0 | N | 22.41% | 1.1236 | 22.41% | N | N
OXFORD | Salem | OXFORD-RURAL | 2523053 | 13 | MARION | Y | OXFORD WR1 | 22.4 | 3.4 | 1.2089 | 14.3 | 0.024 | 0 | N | 1.947% | 1.2089 | 1.947% | N | N
OXFORD | Salem | OXFORD-SHELTON | 2523023 | 13 | MARION | Y | OXFORD WR1 | 22.4 | 3 | 1.3749 | 10.4 | 0.04628 | 0 | N | 3.256% | 1.3749 | 3.256% | N | N
PENINSULA PARK | Portland | PENINSULA PARK-OCKLEY GREEN | 1545021 | 13 | MULTNOMAH | Y | PENINSULA PARK WR1 | 28 | 7.6 | 3.1496 | 17.8 | 0.33184 | 0 | N | 9.532% | 3.1496 | 9.532% | N | N
PENINSULA PARK | Portland | PENINSULA PARK-PENINSULA PARK 13 | 1545011 | 13 | MULTNOMAH | Y | PENINSULA PARK WR1 | 28 | 5.7 | 2.2548 | 17.8 | 0.06716 | 0 | N | 2.892% | 2.2548 | 2.892% | N | N
PLEASANT VALLEY | near Portland | PLEASANT VALLEY-BAXTER | 5553023 | 13 | CLACKAMAS | Y | PLEASANT VALLEY WR1 | 28 | 9.2 | 1.836 | 17.8 | 0.63281 | 0 | N | 25.63% | 1.836 | 25.63% | N | N
PLEASANT VALLEY | near Portland | PLEASANT VALLEY-CLATSOP | 5553053 | 13 | CLACKAMAS | Y | PLEASANT VALLEY WR2 | 28 | 10.9 | 2.012 | 17.8 | 1.0319 | 0 | N | 33.9% | 2.012 | 33.9% | N | N
PLEASANT VALLEY | near Portland | PLEASANT VALLEY-MOON | 5553033 | 13 | CLACKAMAS | Y | PLEASANT VALLEY WR2 | 28 | 10.7 | 3.3029 | 14.3 | 0.59807 | 0 | N | 15.33% | 3.3029 | 15.33% | N | N
PLEASANT VALLEY | near Portland | PLEASANT VALLEY-PLEASANT 13 | 5553013 | 13 | CLACKAMAS | Y | PLEASANT VALLEY WR1 | 28 | 7.3 | 2.357 | 14.3 | 0.40119 | 0 | N | 14.55% | 2.357 | 14.55% | N | N
PLEASANT VALLEY | near Portland | PLEASANT VALLEY-SUN | 5553043 | 13 | CLACKAMAS | Y | PLEASANT VALLEY WR2 | 28 | 13.6 | 4.3176 | 14.3 | 0.89677 | 0 | N | 17.2% | 4.3176 | 17.2% | N | N
PORTSMOUTH | Portland | PORTSMOUTH-CARBIDE | 1558013 | 13 | MULTNOMAH | Y | PORTSMOUTH WR1 | 28 | 9.9 | 3.288 | 17.8 | 0.47449 | 0 | N | 12.61% | 3.288 | 12.61% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 4.9 | 1.2753 | 13.5 | 0 | 0 | N | 0% | 1.2753 | 0% | N | N
PORTSMOUTH | Portland | PORTSMOUTH-WILLIS | 1558033 | 13 | MULTNOMAH | Y | PORTSMOUTH WR1 | 28 | 6.1 | 2.4771 | 14.3 | 0.20501 | 0 | N | 7.644% | 2.4771 | 7.644% | N | N
PROGRESS | near Tigard | PROGRESS-GREENBURG | 4565053 | 13 | WASHINGTON | Y | PROGRESS WR2 | 28 | 11.6 | 3.1556 | 17.8 | 0.29509 | 0 | N | 8.552% | 3.1556 | 8.552% | N | Y
PROGRESS | near Tigard | PROGRESS-HALL | 4565063 | 13 | WASHINGTON | Y | PROGRESS WR1 | 22 | 7.7 | 3.0977 | 17.8 | 0.0079 | 0 | N | 0.2544% | 3.0977 | 0.2544% | N | Y
PROGRESS | near Tigard | PROGRESS-ROBINSON | 4565013 | 13 | WASHINGTON | Y | PROGRESS WR2 | 28 | 9.1 | 3.4981 | 17.8 | 0.16731 | 0 | N | 4.565% | 3.4981 | 4.565% | N | Y
PROGRESS | near Tigard | PROGRESS-SAWYER | 4565023 | 13 | WASHINGTON | Y | PROGRESS WR1 | 22 | 5.2 | 2.4718 | 17.8 | 0.06082 | 0 | N | 2.401% | 2.4718 | 2.401% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 22 | 4.9 | 1.0723 | 11 | 0 | 0 | N | 0% | 1.0723 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 1.4 | 0.48542 | 11 | 0 | 0 | N | 0% | 0.48542 | 0% | N | Y
RALEIGH HILLS | near Portland | RALEIGH HILLS-DOGWOOD | 4570073 | 13 | WASHINGTON | Y | RALEIGH HILLS WR1 | 28 | 8.2 | 3.2579 | 17.8 | 0.16165 | 0 | N | 4.727% | 3.2579 | 4.727% | N | N
RALEIGH HILLS | near Portland | RALEIGH HILLS-MONTCLAIR | 4570053 | 13 | WASHINGTON | Y | RALEIGH HILLS WR1 | 28 | 6 | 1.7403 | 17.8 | 0.86991 | 0 | N | 33.33% | 1.7403 | 33.33% | N | N
RALEIGH HILLS | near Portland | RALEIGH HILLS-OLESON | 4570063 | 13 | WASHINGTON | Y | RALEIGH HILLS WR1 | 28 | 7 | 2.6346 | 17.8 | 0.16269 | 0 | N | 5.816% | 2.6346 | 5.816% | N | N
RAMAPO | near Portland | RAMAPO-EMERALD | 5575023 | 13 | MULTNOMAH | Y | RAMAPO WR1 | 28 | 5.6 | 2.0293 | 17.8 | 0.16647 | 0 | N | 7.581% | 2.0293 | 7.581% | N | N
RAMAPO | near Portland | RAMAPO-GILBERT | 5575013 | 13 | MULTNOMAH | Y | RAMAPO WR1 | 28 | 6.4 | 2.2798 | 17.8 | 0.18813 | 0 | N | 7.623% | 2.2798 | 7.623% | N | N
RAMAPO | near Portland | RAMAPO-RAMAPO 13 | 5575033 | 13 | MULTNOMAH | Y | RAMAPO WR1 | 28 | 11.4 | 3.8815 | 17.8 | 0.4689 | 0 | N | 10.78% | 3.8815 | 10.78% | N | N
REDLAND | near Oregon City | REDLAND-HENRICI | 6581023 | 13 | MULTNOMAH | N | REDLAND WR1 | 22.4 | 7.2 | 2.475 | 17.8 | 0.49563 | 0 | N | 16.68% | 2.475 | 16.68% | N | N
REDLAND | near Oregon City | REDLAND-REDLAND 13 | 6581013 | 13 | MULTNOMAH | N | REDLAND WR1 | 22.4 | 9.1 | 1.15 | 14.3 | 3.4421 | 0 | N | 74.96% | 1.15 | 74.96% | N | N
REEDVILLE | near Beaverton | REEDVILLE-AUGUSTA | 4583083 | 13 | WASHINGTON | Y | REEDVILLE WR2 | 28 | 11.64 | 2.8502 | 17.8 | 1.1577 | 0 | N | 28.89% | 2.8502 | 28.89% | N | Y
REEDVILLE | near Beaverton | REEDVILLE-BLANTON | 4583033 | 13 | WASHINGTON | Y | REEDVILLE WR1 | 28 | 9.11 | 3.2078 | 17.8 | 0.53549 | 0 | N | 14.31% | 3.2078 | 14.31% | N | Y
REEDVILLE | near Beaverton | REEDVILLE-HAZELDALE | 4583013 | 13 | WASHINGTON | Y | REEDVILLE WR1 | 28 | 9.72 | 2.5861 | 17.8 | 0.61028 | 0 | N | 19.09% | 2.5861 | 19.09% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 1.88 | 1.3083 | 18.4 | 0 | 0 | N | 0% | 1.3083 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 0.05 | 0.16789 | 18.4 | 0 | 0 | N | 0% | 0.16789 | 0% | N | Y
REEDVILLE | near Beaverton | REEDVILLE-TV | 4583023 | 13 | WASHINGTON | Y | REEDVILLE WR1 | 28 | 6.42 | 1.8081 | 17.8 | 0.60983 | 0 | N | 25.22% | 1.8081 | 25.22% | N | Y
RIVERGATE SOUTH | near Portland | RIVERGATE SOUTH-11010 | 1598012 | 11.4 | MULTNOMAH | Y | RIVERGATE SOUTH WK2 | 22.4 | 3.9 | 0.49725 | 11 | 0 | 0 | N | 0% | 0.49725 | 0% | N | N
RIVERGATE SOUTH | near Portland | RIVERGATE SOUTH-11011 | 1598022 | 11.4 | MULTNOMAH | Y | RIVERGATE SOUTH WK2 | 22.4 | 5.6 | 2.1009 | 13 | 0.11934 | 0 | N | 5.375% | 2.1009 | 5.375% | N | N
RIVERGATE SOUTH | near Portland | RIVERGATE SOUTH-PEARCY | 1598023 | 13 | MULTNOMAH | Y | RIVERGATE SOUTH WR3 | 22.4 | 8.5 | 1.3336 | 17.8 | 0 | 0 | N | 0% | 1.3336 | 0% | N | N
RIVERGATE SOUTH | near Portland | RIVERGATE SOUTH-SWIFT | 1598013 | 13 | MULTNOMAH | Y | RIVERGATE SOUTH WR3 | 22.4 | 3.4 | 0.78941 | 17.8 | 0 | 0 | N | 0% | 0.78941 | 0% | N | N
RIVERVIEW | Portland | RIVERVIEW-FULTON | 1600033 | 13 | MULTNOMAH | Y | RIVERVIEW WR1 | 28 | 8.4 | 3.1888 | 17.8 | 0.48584 | 0 | N | 13.22% | 3.1888 | 13.22% | N | N
RIVERVIEW | Portland | RIVERVIEW-MACADAM | 1600023 | 13 | MULTNOMAH | Y | RIVERVIEW WR1 | 28 | 7.9 | 3.1503 | 17.8 | 0.1486 | 0 | N | 4.504% | 3.1503 | 4.504% | N | N
RIVERVIEW | Portland | RIVERVIEW-TERWILLIGER | 1600013 | 13 | MULTNOMAH | Y | RIVERVIEW WR1 | 28 | 5.4 | 2.0718 | 17.8 | 0.26922 | 0 | N | 11.5% | 2.0718 | 11.5% | N | N
ROCK CREEK | Portland | ROCK CREEK-185TH | 4598023 | 13 | WASHINGTON | Y | ROCK CREEK WR1 | 28 | 3.49 | 2.4161 | 17.8 | 1.1817 | 0 | N | 32.84% | 2.4161 | 32.84% | Y | Y
ROCK CREEK | Portland | ROCK CREEK-FOREST PARK | 4598033 | 13 | WASHINGTON | Y | ROCK CREEK WR1 | 28 | 10.63 | 1.392 | 18.4 | 0.64388 | 0 | N | 31.63% | 1.392 | 31.63% | Y | Y
ROCK CREEK | Portland | ROCK CREEK-NEWBERRY | 4598013 | 13 | WASHINGTON | Y | ROCK CREEK WR1 | 28 | 12.69 | 1.0998 | 17.8 | 0.41852 | 0 | N | 27.56% | 1.0998 | 27.56% | Y | Y
ROCKWOOD | near Gresham | ROCKWOOD-AIRPORT | 5602053 | 13 | MULTNOMAH | Y | ROCKWOOD WR2 | 22.4 | 3.4 | 1.9291 | 18.4 | 0 | 0 | N | 0% | 1.9291 | 0% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 12.7 | 4.1376 | 18.4 | 0 | 0 | N | 0% | 4.1376 | 0% | N | N
ROCKWOOD | near Gresham | ROCKWOOD-INDUSTRIAL | 5602023 | 13 | MULTNOMAH | Y | ROCKWOOD WR1 | 28 | 9.6 | 2.4371 | 17.8 | 0.04183 | 0 | N | 1.687% | 2.4371 | 1.687% | N | N
ROCKWOOD | near Gresham | ROCKWOOD-REYNOLDS | 5602033 | 13 | MULTNOMAH | Y | ROCKWOOD WR2 | 22.4 | 8.7 | 2.82 | 14.3 | 0.4868 | 0 | N | 14.72% | 2.82 | 14.72% | N | N
ROCKWOOD | near Gresham | ROCKWOOD-ROCKWOOD 13 | 5602013 | 13 | MULTNOMAH | Y | ROCKWOOD WR1 | 28 | 9.2 | 3.4785 | 17.8 | 0.19184 | 0 | N | 5.227% | 3.4785 | 5.227% | N | N
ROCKWOOD | near Gresham | ROCKWOOD-WILKES | 5602043 | 13 | MULTNOMAH | Y | ROCKWOOD WR2 | 22.4 | 4.1 | 0.96087 | 18.4 | 0 | 0 | N | 0% | 0.96087 | 0% | N | N
ROSEMONT | near Lake Oswego | ROSEMONT-HIDDEN SPRINGS | 4604123 | 13 | CLACKAMAS | Y | ROSEMONT WR1 | 28 | 9.3 | 2.014 | 17.8 | 0.58415 | 0 | N | 22.48% | 2.014 | 22.48% | N | Y
ROSEMONT | near Lake Oswego | ROSEMONT-MOSSY BRAE | 4604113 | 13 | CLACKAMAS | Y | ROSEMONT WR1 | 28 | 4.7 | 1.335 | 17.8 | 0.10584 | 0 | N | 7.346% | 1.335 | 7.346% | N | Y
ROSEMONT | near Lake Oswego | ROSEMONT-OVERLOOK | 4604133 | 13 | CLACKAMAS | Y | ROSEMONT WR1 | 28 | 7.3 | 2.2301 | 17.8 | 0.10328 | 0 | N | 4.426% | 2.2301 | 4.426% | N | Y
ROSEWAY | Hillsboro | ROSEWAY-ALEXANDER | 4605033 | 13 | WASHINGTON | Y | ROSEWAY WR1 | 28 | 9.42 | 2.926 | 17.8 | 0.98211 | 0 | N | 25.13% | 2.926 | 25.13% | Y | Y
ROSEWAY | Hillsboro | ROSEWAY-BUTTERNUT | 4605063 | 13 | WASHINGTON | Y | ROSEWAY WR1 | 28 | 0.08 | 0 | 18.4 | 0 | 0 | N | 0% | 0 | 0% | Y | Y
ROSEWAY | Hillsboro | ROSEWAY-CENTURY | 4605043 | 13 | WASHINGTON | Y | ROSEWAY WR1 | 28 | 0.07 | 0 | 18.4 | 0 | 0 | N | 0% | 0 | 0% | Y | Y
ROSEWAY | Hillsboro | ROSEWAY-ESPLANADE | 4605023 | 13 | WASHINGTON | Y | ROSEWAY WR2 | 28 | 8.21 | 2.922 | 17.8 | 0.45454 | 0 | N | 13.46% | 2.922 | 13.46% | Y | Y
ROSEWAY | Hillsboro | ROSEWAY-ROSEWAY 13 | 4605013 | 13 | WASHINGTON | Y | ROSEWAY WR2 | 28 | 8.67 | 2.3347 | 17.8 | 0.64081 | 0 | N | 21.54% | 2.3347 | 21.54% | Y | Y
ROSEWAY | Hillsboro | ROSEWAY-SOHI | 4605053 | 13 | WASHINGTON | Y | ROSEWAY WR2 | 28 | 2.48 | 0.48178 | 18.4 | 0.81817 | 0 | N | 62.94% | 0.48178 | 62.94% | Y | Y
RUBY | Gresham | RUBY-CAR LINE | 5620113 | 13 | MULTNOMAH | Y | RUBY WR1 | 28 | 7.8 | 3.5232 | 17.8 | 0.44394 | 0 | N | 11.19% | 3.5232 | 11.19% | Y | Y
RUBY | Gresham | RUBY-JUNCTION | 5620123 | 13 | MULTNOMAH | Y | RUBY WR1 | 28 | 11.2 | 3.8865 | 17.8 | 0.57091 | 0 | N | 12.81% | 3.8865 | 12.81% | N | Y
SALEM | near Salem | SALEM-13260 | 2637013 | 13 | MARION | Y | SALEM BR1 | 22.4 | 3.2 | 0.72245 | 10.4 | 0 | 0 | N | 0% | 0.72245 | 0% | N | Y
SALEM | near Salem | SALEM-13261 | 2637023 | 13 | MARION | Y | SALEM BR2 | 22.4 | 2 | 0.67608 | 12.6 | 0.099 | 0 | N | 12.77% | 0.67608 | 12.77% | N | Y
SALEM | near Salem | SALEM-13262 | 2637033 | 13 | MARION | Y | SALEM BR2 | 22.4 | 4.8 | 1.8073 | 12.6 | 0.27075 | 0 | N | 13.03% | 1.8073 | 13.03% | N | Y
SALEM | near Salem | SALEM-13263 | 2637043 | 13 | MARION | Y | SALEM BR1 | 22.4 | 3.2 | 1.0479 | 10.4 | 0.02928 | 0 | N | 2.718% | 1.0479 | 2.718% | N | Y
SALEM | near Salem | SALEM-13264 | 2637063 | 13 | MARION | Y | SALEM BR2 | 22.4 | 2 | 0.40846 | 12.6 | 0 | 0 | N | 0% | 0.40846 | 0% | Y | Y
SALEM | near Salem | SALEM-UNION | 2637053 | 13 | MARION | Y | SALEM BR1 | 22.4 | 3.3 | 1.109 | 12.6 | 0.03678 | 0 | N | 3.21% | 1.109 | 3.21% | N | Y
SANDY | Sandy | SANDY-362ND | 5640043 | 13 | CLACKAMAS | Y | SANDY BR1 | 28 | 8.4 | 3.939 | 10.7 | 0.19175 | 0 | N | 4.642% | 3.939 | 4.642% | N | Y
SANDY | Sandy | SANDY-BLUFF | 5640013 | 13 | CLACKAMAS | Y | SANDY BR1 | 28 | 4.8 | 1.5618 | 17.8 | 0.48847 | 0 | N | 23.82% | 1.5618 | 23.82% | Y | Y
SANDY | Sandy | SANDY-SANDY 13 | 5640033 | 13 | CLACKAMAS | Y | SANDY BR1 | 28 | 7.9 | -5.1303 | 17.8 | 10.3487 | 0 | N | 198.3% | -5.1303 | 198.3% | Y | Y
SANDY | Sandy | SANDY-WILDCAT | 5640023 | 13 | CLACKAMAS | Y | SANDY BR1 | 28 | 8.1 | 1.8046 | 10.4 | 2.4837 | 0 | N | 57.92% | 1.8046 | 57.92% | Y | Y
SCHOLLS FERRY | Beaverton | SCHOLLS FERRY-KEMMER | 4645113 | 13 | WASHINGTON | Y | SCHOLLS FERRY WR1 | 28 | 9 | 2.1698 | 17.8 | 0.86425 | 0 | N | 28.49% | 2.1698 | 28.49% | N | N
SCHOLLS FERRY | Beaverton | SCHOLLS FERRY-RAINBOW | 4645123 | 13 | WASHINGTON | Y | SCHOLLS FERRY WR1 | 28 | 5.1 | 1.5077 | 14.3 | 0.75937 | 0 | N | 33.5% | 1.5077 | 33.5% | N | N
SCHOLLS FERRY | Beaverton | SCHOLLS FERRY-ROY ROGERS | 4645133 | 13 | WASHINGTON | Y | SCHOLLS FERRY WR1 | 28 | 12.4 | 2.3122 | 17.8 | 0.9055 | 0 | N | 28.14% | 2.3122 | 28.14% | N | N
SCOGGINS | near Gaston | SCOGGINS-CHERRY GROVE | 4650023 | 13 | WASHINGTON | Y | SCOGGINS BR1 | 3.6 | 1.7 | 0.61169 | 7.4 | 0.10925 | 0 | N | 15.15% | 0.61169 | 15.15% | N | N
SCOGGINS | near Gaston | SCOGGINS-LAURELWOOD | 4650013 | 13 | WASHINGTON | Y | SCOGGINS BR2 | 9.4 | 4.36 | -0.3444 | 7.4 | 2.4414 | 0 | Y | 116.4% | -0.3444 | 116.4% | Y | N
SCOTTS MILLS | Scotts Mills | SCOTTS MILLS-SCOTTS MILLS 13 | 2652013 | 13 | MARION | N | SCOTTS MILLS BR1 | 9.4 | 6.3 | 2.085 | 17.8 | 0.84874 | 2 | Y | 28.93% | 0.085 | 97.1% | N | N
SELLWOOD | Portland | SELLWOOD-KELLOGG PARK | 1655013 | 13 | MULTNOMAH | Y | SELLWOOD WR2 | 28 | 6.501 | 2.7333 | 17.8 | 0.4644 | 0 | N | 14.52% | 2.7333 | 14.52% | N | Y
SELLWOOD | Portland | SELLWOOD-SELLWOOD 13 | 1655033 | 13 | MULTNOMAH | Y | SELLWOOD WR2 | 28 | 11.3 | 4.4483 | 16.8 | 0.52609 | 0 | N | 10.58% | 4.4483 | 10.58% | N | Y
SELLWOOD | Portland | SELLWOOD-WAVERLY | 1655023 | 13 | MULTNOMAH | Y | SELLWOOD WR2 | 28 | 5.3 | 2.1754 | 17.8 | 0.30893 | 0 | N | 12.44% | 2.1754 | 12.44% | N | Y
SHERIDAN | Sheridan | SHERIDAN-EAST | 2660023 | 13 | YAMHILL | Y | SHERIDAN BR1 | 16.8 | 4.7801 | -2.2559 | 17.8 | 5.4108 | 0 | N | 171.5% | -2.2559 | 171.5% | Y | Y
SHERIDAN | Sheridan | SHERIDAN-KADELL | 2660013 | 13 | YAMHILL | Y | SHERIDAN BR1 | 16.8 | 6.0624 | -5.978 | 17.8 | 8.7016 | 2.983 | N | 319.5% | -8.961 | 429% | Y | Y
SHUTE | Hillsboro | SHUTE-BIRCH | 4660064 | 34.5 | WASHINGTON | Y | SHUTE WJ2 | 50 | 1.28 | 0.5382 | 30 | 0 | 0 | N | 0% | 0.5382 | 0% | Y | Y
SHUTE | Hillsboro | SHUTE-FERN | 4660074 | 34.5 | WASHINGTON | Y | SHUTE WJ2 | 50 | 3.74 | 0.39583 | 30 | 0 | 0 | N | 0% | 0.39583 | 0% | Y | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 34.5 | *REDACTED* | Y | *REDACTED* | 50 | 14.31 | 6.7159 | 19 | 0 | 0 | N | 0% | 6.7159 | 0% | N | Y
SHUTE | Hillsboro | SHUTE-MAPLE | 4660084 | 34.5 | WASHINGTON | Y | SHUTE WJ2 | 50 | 14.92 | 9.1504 | 30 | 0 | 0 | N | 0% | 9.1504 | 0% | Y | Y
SHUTE | Hillsboro | SHUTE-PINE | 4660054 | 34.5 | WASHINGTON | Y | SHUTE WJ1 | 50 | 1.06 | 0.0037617 | 60 | 0 | 0 | N | 0% | 0.0037617 | 0% | Y | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 34.5 | *REDACTED* | Y | *REDACTED* | 150 | 21.39 | 1.8756 | 30 | 0 | 0 | N | 0% | 1.8756 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 34.5 | *REDACTED* | Y | *REDACTED* | 150 | 27.57 | 4.0536 | 70 | 0 | 0 | N | 0% | 4.0536 | 0% | N | Y
SHUTE | Hillsboro | SHUTE-SPRUCE | 4660104 | 34.5 | WASHINGTON | Y | SHUTE WJ1 | 50 | 11.93 | 0.0039998 | 70 | 0 | 0 | N | 0% | 0.0039998 | 0% | Y | Y
SILVERTON | Silverton | SILVERTON-NORTH | 2665013 | 13 | MARION | Y | SILVERTON BR2 | 28 | 11.7 | 2.274 | 17.8 | 2.839 | 0 | N | 55.53% | 2.274 | 55.53% | Y | Y
SILVERTON | Silverton | SILVERTON-SOUTH | 2665023 | 13 | MARION | Y | SILVERTON BR1 | 14 | 8.1 | 2.8733 | 17.8 | 0.58803 | 2.125 | N | 16.99% | 0.74827 | 78.38% | Y | Y
SILVERTON | Silverton | SILVERTON-WEST | 2665033 | 13 | MARION | Y | SILVERTON BR2 | 28 | 8.7 | -4.855 | 17.8 | 9.1381 | 0 | N | 213.4% | -4.855 | 213.4% | Y | Y
SIX CORNERS | Six Corners | SIX CORNERS-13359 | 4670013 | 13 | WASHINGTON | Y | SIX CORNERS WR1 | 21 | 12.5 | 3.5021 | 17.8 | 0.92714 | 0 | N | 20.93% | 3.5021 | 20.93% | N | N
SIX CORNERS | Six Corners | SIX CORNERS-13360 | 4670023 | 13 | WASHINGTON | Y | SIX CORNERS WR1 | 21 | 5.2 | 1.8362 | 17.8 | 0.05811 | 0 | N | 3.068% | 1.8362 | 3.068% | N | N
SIX CORNERS | Six Corners | SIX CORNERS-BORCHERS | 4670043 | 13 | WASHINGTON | Y | SIX CORNERS WR2 | 28 | 8.4 | 2.2122 | 17.8 | 0.87915 | 0 | N | 28.44% | 2.2122 | 28.44% | N | N
SIX CORNERS | Six Corners | SIX CORNERS-CHAPMAN | 4670033 | 13 | WASHINGTON | Y | SIX CORNERS WR2 | 28 | 14.8 | 3.4728 | 17.8 | 0.65608 | 0 | N | 15.89% | 3.4728 | 15.89% | N | N
SIX CORNERS | Six Corners | SIX CORNERS-SIX CORNERS 13 | 4670053 | 13 | WASHINGTON | Y | SIX CORNERS WR2 | 28 | 9.8 | 3.8732 | 17.8 | 0.68404 | 0 | N | 15.01% | 3.8732 | 15.01% | N | N
SPRINGBROOK | Newberg | SPRINGBROOK-FERNWOOD | 4672043 | 13 | YAMHILL | Y | SPRINGBROOK WR2 | 28 | 12.0387 | 3.8639 | 17.8 | 0.78964 | 0 | N | 16.97% | 3.8639 | 16.97% | Y | Y
SPRINGBROOK | Newberg | SPRINGBROOK-ST PAUL | 4672023 | 13 | YAMHILL | Y | SPRINGBROOK WR1 | 28 | 5.2 | 1.5988 | 17.8 | 0.62604 | 0 | N | 28.14% | 1.5988 | 28.14% | Y | Y
SPRINGBROOK | Newberg | SPRINGBROOK-VILLA | 4672013 | 13 | YAMHILL | Y | SPRINGBROOK WR1 | 28 | 8.5735 | 3.1552 | 17.8 | 0.77562 | 0 | N | 19.73% | 3.1552 | 19.73% | N | Y
SPRINGBROOK | Newberg | SPRINGBROOK-ZIMRI | 4672063 | 13 | YAMHILL | Y | SPRINGBROOK WR2 | 28 | 6.3409 | 2.5896 | 17.8 | 0.69984 | 0 | N | 21.28% | 2.5896 | 21.28% | Y | Y
ST LOUIS | St.Louis | ST LOUIS-EAST | 2630013 | 13 | MARION | Y | ST LOUIS BR4 | 16 | 10.7004 | 0.52861 | 17.8 | 4.6951 | 0 | N | 89.88% | 0.52861 | 89.88% | N | Y
ST LOUIS | St.Louis | ST LOUIS-NORTH | 2630033 | 13 | MARION | Y | ST LOUIS BR4 | 16 | 5.7588 | -0.79488 | 12.2 | 3.2107 | 0 | N | 132.9% | -0.79488 | 132.9% | Y | Y
ST LOUIS | St.Louis | ST LOUIS-WEST | 2630023 | 13 | MARION | Y | ST LOUIS BR1 | 7.5 | 4.9526 | -0.90837 | 17.8 | 2.4018 | 0 | N | 160.8% | -0.90837 | 160.8% | Y | Y
ST MARYS EAST | near Beaverton | ST MARYS EAST-BETHANY | 4635023 | 13 | WASHINGTON | Y | ST MARYS EAST WR8 | 28 | 6.1 | 2.0983 | 17.8 | 0.0692 | 0 | N | 3.193% | 2.0983 | 3.193% | N | N
ST MARYS EAST | near Beaverton | ST MARYS EAST-BUTNER | 4635053 | 13 | WASHINGTON | Y | ST MARYS EAST WR7 | 28 | 0 | 0 | 17.8 | 0 | 0 | N | 0% | 0 | 0% | N | N
ST MARYS EAST | near Beaverton | ST MARYS EAST-ELMONICA | 4635033 | 13 | WASHINGTON | Y | ST MARYS EAST WR8 | 28 | 10.5 | 3.4098 | 17.8 | 0.35387 | 0 | N | 9.402% | 3.4098 | 9.402% | N | N
ST MARYS EAST | near Beaverton | ST MARYS EAST-JENKINS | 4635013 | 13 | WASHINGTON | Y | ST MARYS EAST WR8 | 28 | 8.4 | 1.733 | 17.8 | 0.98692 | 0 | N | 36.28% | 1.733 | 36.28% | N | N
ST MARYS EAST | near Beaverton | ST MARYS EAST-MILLIKAN | 4635063 | 13 | WASHINGTON | Y | ST MARYS EAST WR7 | 28 | 6.1 | 2.7093 | 14.3 | 0 | 0 | N | 0% | 2.7093 | 0% | N | N
ST MARYS EAST | near Beaverton | ST MARYS EAST-ST MARYS 13 | 4635043 | 13 | WASHINGTON | Y | ST MARYS EAST WR7 | 28 | 0.8 | 0.16737 | 17.8 | 0 | 0 | N | 0% | 0.16737 | 0% | N | N
SULLIVAN | WestLinn | SULLIVAN-ROBINWOOD | 6675013 | 13 | CLACKAMAS | Y | SULLIVAN WR8 | 16.8 | 8.6 | 3.1839 | 17.8 | 0.17023 | 0 | N | 5.075% | 3.1839 | 5.075% | N | N
SULLIVAN | WestLinn | SULLIVAN-SALAMO | 6675053 | 13 | CLACKAMAS | Y | SULLIVAN WR9 | 28 | 7.2 | 1.9873 | 18.4 | 0.24685 | 0 | N | 11.05% | 1.9873 | 11.05% | N | N
SULLIVAN | WestLinn | SULLIVAN-SUSSEX | 6675033 | 13 | CLACKAMAS | Y | SULLIVAN WR8 | 16.8 | 3.7 | 0.93867 | 17.8 | 0.26775 | 0 | N | 22.19% | 0.93867 | 22.19% | N | N
SULLIVAN | WestLinn | SULLIVAN-TANNER | 6675023 | 13 | CLACKAMAS | Y | SULLIVAN WR9 | 28 | 10.7 | 2.7896 | 14.3 | 0.38867 | 0 | N | 12.23% | 2.7896 | 12.23% | N | N
SULLIVAN | WestLinn | SULLIVAN-WILLAMETTE | 6675043 | 13 | CLACKAMAS | Y | SULLIVAN WR9 | 28 | 7.2 | 2.1864 | 17.8 | 0.43749 | 0 | N | 16.67% | 2.1864 | 16.67% | N | N
SUMMIT | Government Camp | SUMMIT-GOVERNMENT CAMP | 5677023 | 13 | CLACKAMAS | Y | SUMMIT FR2 | 14 | 1 | 0.33691 | 7 | 0 | 0 | N | 0% | 0.33691 | 0% | N | N
SUMMIT | Government Camp | SUMMIT-MEADOWS | 5677013 | 13 | CLACKAMAS | Y | SUMMIT FR2 | 14 | 0.6 | 0.22763 | 5 | 0 | 0 | N | 0% | 0.22763 | 0% | N | N
SUMMIT | Government Camp | SUMMIT-SUMMIT 13 | 5677033 | 13 | CLACKAMAS | Y | SUMMIT FR2 | 14 | 1.4 | 0.54847 | 10.7 | 0 | 0 | N | 0% | 0.54847 | 0% | N | N
SUNSET | near Hillsboro | SUNSET-BLANCHET | 4679313 | 13 | WASHINGTON | Y | SUNSET WR3 | 50 | 6.93 | 4.0098 | 17 | 0 | 0 | N | 0% | 4.0098 | 0% | N | Y
SUNSET | near Hillsboro | SUNSET-COLFAX | 4679453 | 13 | WASHINGTON | Y | SUNSET WR4 | 50 | 5.34 | 0.73986 | 17 | 0 | 0 | N | 0% | 0.73986 | 0% | N | Y
SUNSET | near Hillsboro | SUNSET-CORNELL | 4679133 | 13 | WASHINGTON | Y | SUNSET WR1 | 50 | 8.63 | 6.6692 | 15 | 0 | 0 | N | 0% | 6.6692 | 0% | N | Y
SUNSET | near Hillsboro | SUNSET-DAWSON | 4679343 | 13 | WASHINGTON | Y | SUNSET WR3 | 50 | 8.74 | 5.7545 | 17 | 0 | 0 | N | 0% | 5.7545 | 0% | N | Y
SUNSET | near Hillsboro | SUNSET-DORION | 4679123 | 13 | WASHINGTON | Y | SUNSET WR1 | 50 | 3.72 | 2.6359 | 15 | 0 | 0 | N | 0% | 2.6359 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 50 | 5.92 | 4.1902 | 15 | 0 | 0 | N | 0% | 4.1902 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 50 | 4.95 | 2.5596 | 15 | 0 | 0 | N | 0% | 2.5596 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 50 | 2.25 | 0.8 | 17 | 0 | 0 | N | 0% | 0.8 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 50 | 1.21 | 0.098409 | 15 | 0.2503 | 0 | N | 71.78% | 0.098409 | 71.78% | Y | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 50 | 0.5 | 0.067305 | 15 | 0 | 0 | N | 0% | 0.067305 | 0% | Y | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 50 | 0 | 0.092898 | 15 | 0 | 0 | N | 0% | 0.092898 | 0% | Y | Y
SUNSET | near Hillsboro | SUNSET-LANE | 4679223 | 13 | WASHINGTON | Y | SUNSET WR2 | 50 | 7.68 | 4.9634 | 15 | 0 | 0 | N | 0% | 4.9634 | 0% | N | Y
SUNSET | near Hillsboro | SUNSET-MCCALL | 4679433 | 13 | WASHINGTON | Y | SUNSET WR4 | 50 | 10.2 | 6.3954 | 17 | 0 | 0 | N | 0% | 6.3954 | 0% | Y | Y
SUNSET | near Hillsboro | SUNSET-MEEK | 4679423 | 13 | WASHINGTON | Y | SUNSET WR4 | 50 | 8.63 | 4.2674 | 18.4 | 0.10105 | 0 | N | 2.313% | 4.2674 | 2.313% | Y | Y
SUNSET | near Hillsboro | SUNSET-NIXON | 4679413 | 13 | WASHINGTON | Y | SUNSET WR4 | 50 | 2.11 | 1.6404 | 17 | 0 | 0 | N | 0% | 1.6404 | 0% | Y | Y
SUNSET | near Hillsboro | SUNSET-OLCOTT | 4679333 | 13 | WASHINGTON | Y | SUNSET WR3 | 50 | 2.54 | 1.7452 | 17 | 0 | 0 | N | 0% | 1.7452 | 0% | N | Y
SUNSET | near Hillsboro | SUNSET-PAULING | 4679213 | 13 | WASHINGTON | Y | SUNSET WR2 | 50 | 3.8 | 1.4309 | 15 | 0 | 0 | N | 0% | 1.4309 | 0% | N | Y
SUNSET | near Hillsboro | SUNSET-SPALDING | 4679323 | 13 | WASHINGTON | Y | SUNSET WR3 | 50 | 6.25 | 2.2 | 17 | 0.03204 | 1 | N | 1.435% | 1.2 | 46.24% | Y | Y
SUNSET | near Hillsboro | SUNSET-WHITMAN | 4679233 | 13 | WASHINGTON | Y | SUNSET WR2 | 50 | 13.09 | 4.2834 | 15 | 0.41312 | 1 | N | 8.796% | 3.2834 | 30.09% | N | Y
SUNSET | near Hillsboro | SUNSET-YOUNG | 4679113 | 13 | WASHINGTON | Y | SUNSET WR1 | 50 | 5.81 | 4.3235 | 15 | 0.39468 | 0 | N | 8.365% | 4.3235 | 8.365% | N | Y
SWAN ISLAND | Portland | SWAN ISLAND-BASIN | 1680073 | 13 | MULTNOMAH | Y | SWAN ISLAND WR1 | 28 | 6.5 | 1.8387 | 18.4 | 0.1235 | 0 | N | 6.294% | 1.8387 | 6.294% | N | N
SWAN ISLAND | Portland | SWAN ISLAND-DOLPHIN | 1680123 | 13 | MULTNOMAH | Y | SWAN ISLAND WR2 | 28 | 5.5 | 1.1916 | 18.4 | 0.20124 | 0 | N | 14.45% | 1.1916 | 14.45% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 2.8 | 0.85851 | 17.1 | 0 | 0 | N | 0% | 0.85851 | 0% | N | N
SWAN ISLAND | Portland | SWAN ISLAND-GOING | 1680133 | 13 | MULTNOMAH | Y | SWAN ISLAND WR1 | 28 | 6.6 | 1.1736 | 17.8 | 0 | 0 | N | 0% | 1.1736 | 0% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 6.8 | 0.84117 | 18.4 | 0 | 0 | N | 0% | 0.84117 | 0% | N | N
SYLVAN | near Portland | SYLVAN-BARNES | 1685013 | 13 | MULTNOMAH | N | SYLVAN WR1 | 22.4 | 10.42 | 3.52 | 17.8 | 0.33377 | 0 | N | 8.661% | 3.52 | 8.661% | N | N
SYLVAN | near Portland | SYLVAN-PATTON | 1685023 | 13 | MULTNOMAH | N | SYLVAN WR1 | 22.4 | 11.58 | 4.2312 | 17.8 | 0.59185 | 0 | N | 12.27% | 4.2312 | 12.27% | N | N
TABOR | Portland | TABOR-82ND | 1690013 | 13 | MULTNOMAH | Y | TABOR WR6 | 22.4 | 6.1 | 1.9136 | 17.8 | 0.55687 | 0 | N | 22.54% | 1.9136 | 22.54% | Y | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 22.4 | 9.6 | 4.2078 | 16.8 | 0.067655 | 0 | N | 1.582% | 4.2078 | 1.582% | N | Y
TABOR | Portland | TABOR-TABOR 13 | 1690023 | 13 | MULTNOMAH | Y | TABOR WR6 | 22.4 | 9.1 | 3.1758 | 16.8 | 0.7164 | 0 | N | 18.41% | 3.1758 | 18.41% | N | Y
TEKTRONIX | Beaverton | TEKTRONIX-DUCKS | 4693093 | 13 | WASHINGTON | Y | TEKTRONIX WR3 | 28 | 5.7 | 0.9677 | 18.4 | 0 | 0 | N | 0% | 0.9677 | 0% | Y | Y
TEKTRONIX | Beaverton | TEKTRONIX-HOCKEN | 4693063 | 13 | WASHINGTON | Y | TEKTRONIX WR2 | 28 | 2.6 | 1.039 | 14.3 | 0.11613 | 0 | N | 10.05% | 1.039 | 10.05% | N | Y
TEKTRONIX | Beaverton | TEKTRONIX-MEADOW | 4693083 | 13 | WASHINGTON | Y | TEKTRONIX WR3 | 28 | 9 | 2.7469 | 18.4 | 0.62687 | 0 | N | 18.58% | 2.7469 | 18.58% | Y | Y
TEKTRONIX | Beaverton | TEKTRONIX-NORTH | 4693053 | 13 | WASHINGTON | Y | TEKTRONIX WR2 | 28 | 5.1 | 2.3267 | 14.3 | 0 | 0 | N | 0% | 2.3267 | 0% | N | Y
TEKTRONIX | Beaverton | TEKTRONIX-SHANNON | 4693033 | 13 | WASHINGTON | Y | TEKTRONIX WR1 | 28 | 9 | 3.4206 | 18.4 | 0.29775 | 0 | N | 8.008% | 3.4206 | 8.008% | N | Y
TEKTRONIX | Beaverton | TEKTRONIX-SOUTH | 4693043 | 13 | WASHINGTON | Y | TEKTRONIX WR2 | 28 | 11.3 | 4.0439 | 17.8 | 0.53248 | 0 | N | 11.64% | 4.0439 | 11.64% | N | Y
TEKTRONIX | Beaverton | TEKTRONIX-TEKTRONIX 13 | 4693023 | 13 | WASHINGTON | Y | TEKTRONIX WR1 | 28 | 10.3 | 3.9631 | 17.8 | 0.16084 | 0 | N | 3.9% | 3.9631 | 3.9% | N | Y
TEKTRONIX | Beaverton | TEKTRONIX-TERMAN | 4693073 | 13 | WASHINGTON | Y | TEKTRONIX WR3 | 28 | 3.8 | 0.34828 | 18.4 | 0 | 0 | N | 0% | 0.34828 | 0% | Y | Y
TEKTRONIX | Beaverton | TEKTRONIX-WEST | 4693013 | 13 | WASHINGTON | Y | TEKTRONIX WR1 | 28 | 3.1 | 0.98105 | 14.3 | 0 | 0 | N | 0% | 0.98105 | 0% | N | Y
TEMP H | Portland | TEMP H-NEPTUNE | 8003112 | 11.1 | 0 | N | TEMP H TBD | 22 | 5.6 | 2.2702 | 15.2 | 0 | 0 | N | 0% | 2.2702 | 0% | N | N
TEMP H | Portland | TEMP H-SATURN | 8003122 | 11.1 | 0 | N | TEMP H TBD | 22 | 1 | 0.4047 | 15.2 | 0 | 0 | N | 0% | 0.4047 | 0% | N | N
TIGARD | Tigard | TIGARD-13336 | 4695013 | 13 | WASHINGTON | Y | TIGARD WR1 | 16.8 | 5.1 | 1.6643 | 17.8 | 0.07303 | 0 | N | 4.204% | 1.6643 | 4.204% | N | N
TIGARD | Tigard | TIGARD-13337 | 4695043 | 13 | WASHINGTON | Y | TIGARD WR1 | 16.8 | 5 | 1.9442 | 17.8 | 0.21783 | 0 | N | 10.07% | 1.9442 | 10.07% | N | N
TIGARD | Tigard | TIGARD-13361 | 4695023 | 13 | WASHINGTON | Y | TIGARD WR2 | 28 | 4 | 1.2096 | 17.8 | 0.091315 | 0 | N | 7.019% | 1.2096 | 7.019% | N | N
TIGARD | Tigard | TIGARD-13362 | 4695033 | 13 | WASHINGTON | Y | TIGARD WR2 | 28 | 10 | 2.3088 | 17.8 | 0.5779 | 0 | N | 20.02% | 2.3088 | 20.02% | N | N
TIGARD | Tigard | TIGARD-TIGARD 13 | 4695053 | 13 | WASHINGTON | Y | TIGARD WR2 | 28 | 7.9 | 2.7627 | 17.8 | 0.51376 | 0 | N | 15.68% | 2.7627 | 15.68% | N | N
TOWN CENTER | Portland | TOWN CENTER-LAWNFIELD | 6696023 | 13 | CLACKAMAS | Y | TOWN CENTER WR2 | 28 | 6.536 | 4.7358 | 17.8 | 0.07498 | 0 | N | 1.559% | 4.7358 | 1.559% | N | N
TOWN CENTER | Portland | TOWN CENTER-MONTEREY | 6696053 | 13 | CLACKAMAS | Y | TOWN CENTER WR1 | 28 | 9.033 | 3.9747 | 17.8 | 0.18976 | 0 | N | 4.557% | 3.9747 | 4.557% | N | N
TOWN CENTER | Portland | TOWN CENTER-NORTH | 6696073 | 13 | CLACKAMAS | Y | TOWN CENTER WR2 | 28 | 2.5 | 0.52851 | 11 | 0 | 0 | N | 0% | 0.52851 | 0% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 5.604 | 2.3524 | 14.3 | 0 | 0 | N | 0% | 2.3524 | 0% | N | N
TOWN CENTER | Portland | TOWN CENTER-SOUTH | 6696013 | 13 | CLACKAMAS | Y | TOWN CENTER WR1 | 28 | 4.1 | 0.96661 | 11 | 0 | 0 | N | 0% | 0.96661 | 0% | N | N
TOWN CENTER | Portland | TOWN CENTER-SUNNYBROOK | 6696063 | 13 | CLACKAMAS | Y | TOWN CENTER WR2 | 28 | 7.8 | 2.6395 | 17.8 | 0.19156 | 0 | N | 6.766% | 2.6395 | 6.766% | N | N
TOWN CENTER | Portland | TOWN CENTER-VALLEY VIEW | 6696033 | 13 | CLACKAMAS | Y | TOWN CENTER WR1 | 28 | 8.3 | 3.5754 | 17.8 | 0.01727 | 0 | N | 0.4807% | 3.5754 | 0.4807% | N | N
TUALATIN | Tualatin | TUALATIN-AVERY | 4697023 | 13 | WASHINGTON | Y | TUALATIN WR2 | 28 | 9.7 | 2.696 | 17.8 | 0.69548 | 0 | N | 20.51% | 2.696 | 20.51% | N | N
TUALATIN | Tualatin | TUALATIN-CIPOLE | 4697063 | 13 | WASHINGTON | Y | TUALATIN WR2 | 28 | 13.8 | 3.6099 | 17.8 | 0.23915 | 0 | N | 6.213% | 3.6099 | 6.213% | N | N
TUALATIN | Tualatin | TUALATIN-HERMAN | 4697043 | 13 | WASHINGTON | Y | TUALATIN WR1 | 28 | 5.3 | 1.0516 | 17.8 | 0.29753 | 0 | N | 22.05% | 1.0516 | 22.05% | N | N
TUALATIN | Tualatin | TUALATIN-IBACH | 4697013 | 13 | WASHINGTON | Y | TUALATIN WR2 | 28 | 6.8 | 1.6714 | 17.8 | 0.4287 | 0 | N | 20.41% | 1.6714 | 20.41% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 13.4 | 6.5102 | 18.4 | 0 | 0 | N | 0% | 6.5102 | 0% | N | N
TUALATIN | Tualatin | TUALATIN-TUALATIN 13 | 4697033 | 13 | WASHINGTON | Y | TUALATIN WR1 | 28 | 6.7 | 1.6631 | 17.8 | 0.11226 | 0 | N | 6.323% | 1.6631 | 6.323% | N | N
TURNER | Turner | TURNER-CASCADE | 2698023 | 13 | MARION | N | TURNER WR1 | 8.4 | 3.2 | 0.04 | 14.3 | 2.5286 | 0 | N | 98.44% | 0.04 | 98.44% | Y | N
TURNER | Turner | TURNER-TURNER 13 | 2698013 | 13 | MARION | N | TURNER WR1 | 8.4 | 5.6 | 1.705 | 14.3 | 0.6892 | 0 | N | 28.79% | 1.705 | 28.79% | N | N
TWILIGHT | Canby | TWILIGHT-BREMER | 6699033 | 13 | CLACKAMAS | Y | TWILIGHT BR1 | 28 | 5.3 | 1.9965 | 17.8 | 0.55701 | 0 | N | 21.81% | 1.9965 | 21.81% | N | N
UNIONVALE | Dayton | UNIONVALE-UNIONVALE 13 | 4700013 | 13 | YAMHILL | N | UNIONVALE BR1 | 7.5 | 5.485 | 1.83 | 10.7 | 0.48873 | 0 | N | 21.08% | 1.83 | 21.08% | N | N
UNIVERSITY | Salem | UNIVERSITY-MILL | 2705013 | 13 | MARION | N | UNIVERSITY WR3 | 22.4 | 6.1 | 3.595 | 17.8 | 0.0263 | 0 | N | 0.7263% | 3.595 | 0.7263% | N | N
UNIVERSITY | Salem | UNIVERSITY-TRADE | 2705023 | 13 | MARION | N | UNIVERSITY WR3 | 22.4 | 6.1 | 2.715 | 17.8 | 0.15441 | 0 | N | 5.381% | 2.715 | 5.381% | N | N
URBAN | Portland | URBAN-BARBUR | 1707053 | 13 | MULTNOMAH | Y | URBAN WR2 | 22.4 | 0.6 | 0.10242 | 17.8 | 0.00568 | 0 | N | 5.254% | 0.10242 | 5.254% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 9.2 | 3.0972 | 17.8 | 0 | 0 | N | 0% | 3.0972 | 0% | N | Y
URBAN | Portland | URBAN-CORBETT | 1707013 | 13 | MULTNOMAH | Y | URBAN WR1 | 28 | 3.3 | 1.1138 | 10.4 | 0.09389 | 0 | N | 7.774% | 1.1138 | 7.774% | N | Y
URBAN | Portland | URBAN-GAINES | 1707063 | 13 | MULTNOMAH | Y | URBAN WR3 | 28 | 7.2 | 3.405 | 10.4 | 0.033235 | 0 | N | 0.9666% | 3.405 | 0.9666% | N | Y
URBAN | Portland | URBAN-GIBBS | 1707043 | 13 | MULTNOMAH | Y | URBAN WR1 | 28 | 1.6 | 0.78864 | 10.4 | 0.04833 | 0 | N | 5.774% | 0.78864 | 5.774% | N | Y
URBAN | Portland | URBAN-KELLY | 1707073 | 13 | MULTNOMAH | Y | URBAN WR2 | 22.4 | 3.5 | 1.3511 | 17.8 | 0.16005 | 0 | N | 10.59% | 1.3511 | 10.59% | Y | Y
URBAN | Portland | URBAN-LANDING | 1707023 | 13 | MULTNOMAH | Y | URBAN WR3 | 28 | 2.7 | 1.1559 | 13.7 | 0 | 0 | N | 0% | 1.1559 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 6.1 | 2.8056 | 14.3 | 0 | 0 | N | 0% | 2.8056 | 0% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 22.4 | 6.6 | 3.9958 | 17.8 | 0 | 0 | N | 0% | 3.9958 | 0% | N | Y
TEMP B | Portland | TEMP B-NORTH | 1707103 | 13 | MULTNOMAH | Y | TEMP B WR20 | 28 | 0 | 0 | 17.8 | 0 | 0 | N | 0% | 0 | 0% | N | N
TEMP B | Portland | TEMP B-SOUTH | 1707113 | 13 | MULTNOMAH | Y | TEMP B WR20 | 28 | 0.5 | 0 | 17.8 | 0 | 0 | N | 0% | 0 | 0% | N | N
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 15.6 | 13.2 | 0.89136 | 17.8 | 0.19712 | 0 | N | 18.11% | 0.89136 | 18.11% | N | N
WACONDA | near Hopmere | WACONDA-RIVER | 2720023 | 13 | MARION | Y | WACONDA BR1 | 25 | 6.4 | 1.0639 | 17.8 | 0.31186 | 0 | Y | 22.67% | 1.0639 | 22.67% | N | N
WACONDA | near Hopmere | WACONDA-WACONDA 13 | 2720013 | 13 | MARION | Y | WACONDA BR1 | 25 | 7.9 | 0.45415 | 14.3 | 3.3385 | 2.49 | Y | 88.03% | -2.0359 | 153.7% | Y | N
WALLACE | Salem | WALLACE-WALLACE 13 | 2725013 | 13 | POLK | Y | WALLACE BR1 | 28 | 5.3 | -0.45298 | 14.3 | 2.8548 | 5.47 | N | 118.9% | -5.923 | 346.6% | Y | Y
WALLACE | Salem | WALLACE-WILLOW LAKE | 2725023 | 13 | POLK | Y | WALLACE BR1 | 28 | 5.4 | 1.1343 | 14.3 | 0.10052 | 0 | N | 8.141% | 1.1343 | 8.141% | Y | Y
WELCHES | near Welches | WELCHES-WELCHES 13 | 5727013 | 13 | CLACKAMAS | Y | WELCHES BR3 | 10.5 | 4.7 | 2.0314 | 10.4 | 0.01156 | 0 | N | 0.5658% | 2.0314 | 0.5658% | N | N
WELCHES | near Welches | WELCHES-ZIG ZAG | 5727023 | 13 | CLACKAMAS | Y | WELCHES BR1 | 7.5 | 2.2 | 0.96509 | 7.3 | 0.02423 | 0 | N | 2.449% | 0.96509 | 2.449% | N | N
WEST PORTLAND | Lower Yard near Tigard | WEST PORTLAND-72ND | 4735033 | 13 | WASHINGTON | Y | WEST PORTLAND WR2 | 28 | 10.1 | 4.0019 | 17.8 | 0.5839 | 0 | N | 12.73% | 4.0019 | 12.73% | N | N
WEST PORTLAND | Lower Yard near Tigard | WEST PORTLAND-NORTH | 4735043 | 13 | WASHINGTON | Y | WEST PORTLAND WR2 | 28 | 7.6 | 2.5681 | 17.8 | 0.28228 | 0 | N | 9.903% | 2.5681 | 9.903% | N | N
WEST PORTLAND | Lower Yard near Tigard | WEST PORTLAND-PACIFIC | 4735023 | 13 | WASHINGTON | Y | WEST PORTLAND WR1 | 28 | 9.9 | 3.7778 | 17.8 | 0.24027 | 0 | N | 5.98% | 3.7778 | 5.98% | N | N
WEST PORTLAND | Lower Yard near Tigard | WEST PORTLAND-WEST PORTLAND 13 | 4735013 | 13 | WASHINGTON | Y | WEST PORTLAND WR1 | 28 | 8.8 | 2.2643 | 17.8 | 0.57405 | 0 | N | 20.22% | 2.2643 | 20.22% | N | N
WEST UNION | near Hillsboro | WEST UNION-ALOCLEK | 4737033 | 13 | WASHINGTON | Y | WEST UNION WR2 | 28 | 5.69 | 3.6811 | 18.4 | 0 | 0 | N | 0% | 3.6811 | 0% | Y | Y
WEST UNION | near Hillsboro | WEST UNION-CORNELIUS PASS | 4737013 | 13 | WASHINGTON | Y | WEST UNION WR1 | 28 | 4.61 | 1.4961 | 17.8 | 0.69137 | 0 | N | 31.61% | 1.4961 | 31.61% | Y | Y
WEST UNION | near Hillsboro | WEST UNION-IMBRIE | 4737053 | 13 | WASHINGTON | Y | WEST UNION WR2 | 28 | 11.38 | 7.9537 | 18.4 | 0 | 0 | N | 0% | 7.9537 | 0% | Y | Y
WEST UNION | near Hillsboro | WEST UNION-JACOBSON | 4737043 | 13 | WASHINGTON | Y | WEST UNION WR2 | 28 | 9.63 | 3.3448 | 18.4 | 0.16569 | 0 | N | 4.72% | 3.3448 | 4.72% | Y | Y
WEST UNION | near Hillsboro | WEST UNION-WEST UNION 13 | 4737023 | 13 | WASHINGTON | Y | WEST UNION WR1 | 28 | 11.41 | 4.585 | 17.8 | 0.44212 | 0 | N | 8.795% | 4.585 | 8.795% | Y | Y
WILLAMINA | near Willamina | WILLAMINA-BRIDGE | 2740033 | 13 | POLK | Y | WILLAMINA BR1 | 16.8 | 3.1107 | -1.1239 | 9.9 | 3.1558 | 0 | N | 155.3% | -1.1239 | 155.3% | Y | Y
WILLAMINA | near Willamina | WILLAMINA-BUELL | 2740023 | 13 | POLK | Y | WILLAMINA BR1 | 16.8 | 3.5 | -0.91709 | 10.4 | 3.176 | 7.8 | N | 140.6% | -8.7171 | 485.9% | Y | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 14 | 6.2906 | 0.2678 | 13.7 | 0 | 0 | N | 0% | 0.2678 | 0% | N | N
WILLBRIDGE | Portland | WILLBRIDGE-SALMONBERRY | 1741052 | 13 | MULTNOMAH | Y | WILLBRIDGE WR1 | 28 | 3 | 0.83735 | 14.7 | 0 | 0 | N | 0% | 0.83735 | 0% | N | N
WILLBRIDGE | Portland | WILLBRIDGE-WILDWOOD | 1741062 | 13 | MULTNOMAH | Y | WILLBRIDGE WR1 | 28 | 6 | 1.5767 | 9.1 | 0.02592 | 0 | N | 1.617% | 1.5767 | 1.617% | N | N
WILSONVILLE | near Wilsonville | WILSONVILLE-BOECKMAN | 4745073 | 13 | CLACKAMAS | Y | WILSONVILLE WR1 | 28 | 5.9 | 1.4021 | 17.8 | 0.55179 | 0 | N | 28.24% | 1.4021 | 28.24% | N | Y
WILSONVILLE | near Wilsonville | WILSONVILLE-CHARBONNEAU | 4745063 | 13 | CLACKAMAS | Y | WILSONVILLE WR1 | 28 | 11.5 | 2.2897 | 18.4 | 2.6917 | 0.3 | N | 54.03% | 1.9897 | 60.06% | N | Y
WILSONVILLE | near Wilsonville | WILSONVILLE-CITY | 4745013 | 13 | CLACKAMAS | Y | WILSONVILLE WR3 | 28 | 11.8 | 4.5288 | 18.4 | 0.14532 | 0 | N | 3.109% | 4.5288 | 3.109% | N | Y
*REDACTED* | *REDACTED* | *REDACTED* | *REDACTED* | 13 | *REDACTED* | Y | *REDACTED* | 28 | 8.7 | 4.9484 | 18.4 | 0 | 1.83 | N | 0% | 3.1184 | 36.98% | Y | Y
WILSONVILLE | near Wilsonville | WILSONVILLE-PARKWAY | 4745023 | 13 | CLACKAMAS | Y | WILSONVILLE WR3 | 28 | 7.8 | 2.8404 | 18.4 | 0 | 0 | N | 0% | 2.8404 | 0% | Y | Y
WILSONVILLE | near Wilsonville | WILSONVILLE-VILLEBOIS | 4745033 | 13 | CLACKAMAS | Y | WILSONVILLE WR1 | 28 | 9.7 | 2.7543 | 17.8 | 0.64934 | 0 | N | 19.08% | 2.7543 | 19.08% | N | Y
WILSONVILLE | near Wilsonville | WILSONVILLE-WEST | 4745093 | 13 | CLACKAMAS | Y | WILSONVILLE WR2 | 28 | 12.6 | 4.464 | 18.4 | 0.6602 | 0 | N | 12.88% | 4.464 | 12.88% | N | Y
WOODBURN | Woodburn | WOODBURN-CANNERY | 2753033 | 13 | MARION | Y | WOODBURN BR1 | 28 | 12.3469 | 2.3264 | 17.8 | 0.49507 | 0 | N | 17.55% | 2.3264 | 17.55% | N | N
WOODBURN | Woodburn | WOODBURN-EAST | 2753013 | 13 | MARION | Y | WOODBURN BR2 | 14 | 4.3201 | -4.4665 | 10.4 | 6.9676 | 0 | N | 278.6% | -4.4665 | 278.6% | Y | Y
WOODBURN | Woodburn | WOODBURN-TOMLIN | 2753023 | 13 | MARION | Y | WOODBURN BR1 | 28 | 7.9 | 0.99706 | 10.4 | 3.2906 | 0 | N | 76.75% | 0.99706 | 76.75% | N | N
WOODBURN | Woodburn | WOODBURN-WEST | 2753043 | 13 | MARION | Y | WOODBURN BR2 | 14 | 6.1922 | 2.6482 | 17.8 | 0.27649 | 0 | N | 9.454% | 2.6482 | 9.454% | N | Y
YAMHILL | near Yamhill | YAMHILL-CARLTON | 4760023 | 13 | YAMHILL | N | YAMHILL BR2 | 7.8 | 7.655 | 2.68 | 10.4 | 0.9599 | 0 | N | 26.37% | 2.68 | 26.37% | N | N
YAMHILL | near Yamhill | YAMHILL-YAMHILL 13 | 4760013 | 13 | YAMHILL | N | YAMHILL BR1 | 7.5 | 5.175 | 2.55 | 17.8 | 1.1767 | 2.5 | Y | 31.58% | 0.05 | 98.66% | Y | N