## PGE Option Parameters (2017)
|  | Design Basis Parameters | [5 empty] | Technical/Performance Parameters | [14 empty] | Financial Parameters | [12 empty] | Energy Storage Parameters
No. | Supply-Side Option | Option Design Basis | Duty | Net Capacity (MW)(1) | Average Design Life Net Capacity, Including Degradation (MW) | Capacity Factor (%) | Primary Fuel | Land Required (acres/MW)(2) | Net Plant Heat Rate (Btu/kWh-HHV) | Average Design Life Net Plant Heat Rate, Including Degradation (Btu/kWh-HHV) | Heat Rate vs Output (Btu/kWh versus kW-net, New and Clean) | Fuel Consumption versus Output (MMBtu/hr-HHV versus kW-net, New and Clean)(3) | Minimum Turndown Capacity (%)(4) | Ramp Rate (MW/min) | Minimum Run/Down Times (hours) | Start Time to Full Load (mins) (5) | Water Consumption (MGD) | Scheduled Maintenance (weeks/yr) (6) | Equivalent Forced Outage Rate (%) | EPC Period(7) (months) | No. | Supply-Side Option | Design Life (years) | Expenditure Pattern (by month/qtr) | Overnight EPC Capital Cost ($000, 2017$) | Owner's Cost Allowance (8) (%) | Overnight Total Capital Cost ($000, 2017$) | Overnight Total Capital Cost Standard Deviation, 1σ ($,000, 2017$) | Fixed O&M Cost (2017$/kW-year)(9) | Nonfuel Variable O&M Cost (2017$/MWh) (9) | Nonfuel Variable Wear and Tear Costs (2017$/MWh)(10) | Capital Additions/ Maintenance Accrual (2017$/yr) | Nonfuel Startup Variable O&M Costs (2017$/start)(11) | Fuel Startup Variable O&M Usage (MMBtu-HHV/start)(12) | Decommissioning Cost ($000, 2017$)(13) | Energy Capacity (MWh) | Round Trip Efficiency (%)
1 | 1x0 GE 7F.05 | Combustion Turbine: GE 7F.05 Emissions Control: SCR, CO catalyst | Peaking | 231 | 218 | 11% | Natural Gas | 0.043478 | 9830 | 10170 | See Next Column | y = 1.657E-08x2 + 1.883E-03x + 9.521E+02 | 43% | 40 | 0.5 / 0.5 | 11 | 0 | 1.8 | 4% | 24 | 2 | 1x0 GE 7F.05 | 30 | Refer to Appendix B | 115000 | 25% | 143750 | 10800 | 6.7 | 6.9 | 6.7 | Refer to Note 18 | 4 | 295 | 1380 | n/a | n/a
2 | 6x0 Wartsila 18V50SG | Recip. Engine: Wartsila 18V50SG Heat Rejection: Wet Cooling Tower Emissions Control: SCR, CO catalyst | Peaking | 110 | 107 | 25% | Natural Gas | 0.063636 | 8300 | 8470 | See Next Column | y = -3.336E-09x2 + 7.875E-03x + 8.800E+01 | 25% | 84 | 0.5 / 0.5 | 10 | 0.36 | 0.9 | 2.2% | 24 | 3 | 6x0 Wartsila 18V50SG | 30 | Refer to Appendix B | 116000 | 25% | 145000 | 10900 | 11 | 7.2 | 6.25 | Refer to Note 18 | 11 | 72 | 1260 | n/a | n/a
3 | 1x1 GE 7HA.01 | Combustion Turbine: GE 7HA.01 Duct Firing: None Emissions Control: SCR, CO catalyst Heat Rejection: Wet Cooling Tower | Intermediate | 424 | 400 | 70% | Natural Gas | 0.0375 | 6290 | 6450 | See Next Column | y = 1.638E-09x2 + 4.583E-03x + 4.283E+02 | 33% | 55 | 1.5 / 1.5 | Hot: 60 Warm: 100 Cold: 210 | 1.9 | 3.9 | 2.9% | 30 | 5 | 1x1 GE 7HA.01 | 30 | Refer to Appendix B | 449000 | 25% | 561250 | 56200 | 7.4 | 3.3 | 2.7 | Refer to Note 18 | 370 | 950 | 9770 | n/a | n/a
4 | Biomass Combustion | Boiler: Bubbling Fluidized Bed Emissions Control: SNCR, Fabric Filter Heat Rejection: Wet Cooling Tower | Baseload | 35 | 35 | 85% | Wood | 1 | 13000 | 13350 | y = 3.918E-06x2 - 0.3086x + 19,000 | n/a | 25% | 1.75 | 8.0 / 8.0 | 180 | 1 | 3.83 | 7.5% | 36 | 7 | Biomass Combustion | 40 | Refer to Appendix B | 170800 | 25% | 213500 | 32000 | 145 | 9.6 | n/a | Refer to Note 18 | n/a | n/a | 2080 | n/a | n/a
5 | Geothermal -- Binary | System: Binary Geothermal System Heat Rejection: Air-Cooled Condenser | Baseload | 35 | n/a | 85% | n/a | 1 | n/a | n/a | Refer to Note 21 | n/a | 50% | 4.5 | 0.5 / 0.5 | 10 | 0.2 | 3.83 | 6% | 24(16) | 8 | Geothermal -- Binary | 30 | Refer to Appendix B | 235700 | 20% | 282800 | 70700 | 110 | 16.8 | n/a | Refer to Note 18 | n/a | n/a | 3940 | n/a | n/a
6 | Battery Storage -- Lithium Ion | Battery: Lithium Ion Discharge Duration: 2 hrs | Storage | 50 | n/a | n/a | n/a | 0.04(14) | n/a | n/a | n/a | n/a | 0% | Refer to Note 15 | n/a | n/a | n/a | 2 | n/a | 12 to 15 | 10 | Battery Storage -- Lithium Ion | 20(17) | Refer to Appendix B | 71000 | 12% | 79500 | 9900 | 12 | n/a | n/a | 200,000(19) | n/a | n/a | 1240 | 100 | 85
7 | Battery Storage -- Redox Flow | Battery: Redox Flow Discharge Duration: 6 hrs | Storage | 10 | n/a | n/a | n/a | 0.16(14) | n/a | n/a | n/a | n/a | 0% | Refer to Note 15 | n/a | n/a | n/a | 2 | n/a | 12 to 15 | 11 | Battery Storage -- Redox Flow | 20(17) | Refer to Appendix B | 36700 | 12% | 41100 | 5100 | 30 | n/a | n/a | 45,000(19) | n/a | n/a | 640 | 60 | 75
NOTES:
(1) Performance parameters assume ISO conditions (59 ͦ F, 60% relative humidity, and sea level elevation). Net capacity is defined as the nameplate (or gross) unit capacity, minus any auxiliary losses.
(2) Typical value; actual value is specific to project, location, and owner's requirements.
(3) For combustion turbines and reciprocating engines, heat rate is a function of output as well as fuel consumption. In Black & Veatch's experience, providing a curve showing fuel consumption as a function of output provides a more accurate result. The curve provided is Fuel Consumption versus Output (MMBtu-HHV versus kW-net, New and Clean). Heat rate can be further determined by dividing fuel consumption by output.
(4) While maintaining emissions compliance for Options 1 through 7.
(5) Start times exclude purge time. Combined cycle start time definitions: Hot start is defined as a start after an 8 hour shutdown (generally considered 8 hours or less). Warm start is defined as a start after a 48 hour shutdown (generally considered 8 to 48 hours). Cold start is defined as a start when the steam turbine rotor temperature is at or near atmospheric temperature (generally considered greater than 48 hours).
(6) Natural gas fueled option maintenance values are annual averages based on prime mover (combustion turbine or reciprocating engine) manufacturer recommended maintenance, excluding annual outages. Renewable option maintenance based on industry norms.
(7) The project duration period starts with EPC contractor notice to proceed (NTP) and ends at the commercial operation date (COD). Some excluded activities are permitting and EPC specification development.
(8) Owner's cost allowance includes costs associated with project development, operating spare parts and plant equipment, owner's contingencies and project management, utility interconnections, taxes, and legal fees. The owner's cost allowance can vary widely.
(9) Estimates expressed in terms of new and clean condition.
(10) Estimated wear and tear costs include annualized estimated variable maintenance costs on the turbines, generators,steam generator, batteries, and SCR catalysts, as applicable.
(11) Assumes average start. Includes makeup water and chemicals. Does not include fuel or electricity.
(12) Startup fuel consumption for achieving CTG/RICE full load operation.
(13) Decommissioning costs are typically accrued annually over the design life of the asset to decommission the facility. Total project decommissioning costs are provided in 2017 USD. For all SSOs, the site would be returned to a brownfield condition at the end of its design life.
(14) For battery energy storage systems (BESS), 1 acre can accommodate approximately 40 to 60 MWh of energy storage capacity. Therefore, a 50 MW¦100 MWh system would require approximately 2 acres and a 10 MW¦40 MWh system would require approximately 1 acre.
(15) BESS are able to ramp up from an idle status to full rated capacity in less than 1 second.
(16) EPC period for geothermal projects is considered 24 months for construction of generation systems. Project development, including drilling of test wells and associated well development activities, is assumed to require 24 months, but development is assumed to be conducted prior to the EPC period.
(17) Design life for battery energy storage options is consistent with the warranties/guarantees provided by battery OEMs and is consistent with the capacity maintenance costs listed in the Table.
(18) Operation of certain SSOs requires periodic replacement of specific systems or equipment (either dependent upon number of years in service or hours of operation). In instances where these periodic costs are necessary (for the SSOs under consideration in this report), these costs have been included in the relevant O&M costs associated with specific technology options.
(19) The cost per year presented here assumes 365 cycles per year at 80% depth of discharge (DoD) for both technologies. For lithium ion, the degradation per year is approximately 1.8%. For vanadium redox, the degradation is less than 1% per year.
(20) Daily storage based on the 8 hours of discharge per day.
(21) Geothermal resources typically degrade at about -1.5degF per year. This is typically accounted for via decrease in net power output, which may be mitigated somewhat by additional well that is drilled once per five years.

## AppC - Forecast Factors (2017)
Total Capital Cost Forecast Factors by Technology (Constant Dollar Basis)
Technology | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
Coal with 30% CCS | 1 | 1.0017 | 0.99583 | 0.99086 | 0.9847 | 0.97707 | 0.96691 | 0.95601 | 0.94364 | 0.92836 | 0.91467 | 0.90304 | 0.89232 | 0.88159 | 0.87109 | 0.8609 | 0.85195 | 0.84356 | 0.83458 | 0.82568 | 0.81733
Coal with 90% CCS | 1 | 1.0017 | 0.99583 | 0.99086 | 0.9847 | 0.97707 | 0.96691 | 0.95601 | 0.94364 | 0.92836 | 0.91467 | 0.90304 | 0.89232 | 0.88159 | 0.87109 | 0.8609 | 0.85195 | 0.84356 | 0.83458 | 0.82568 | 0.81733
Combustion Turbine | 1 | 1.0036 | 0.99963 | 0.99655 | 0.99227 | 0.9865 | 0.97815 | 0.96905 | 0.95841 | 0.94479 | 0.93273 | 0.92275 | 0.91366 | 0.90454 | 0.89562 | 0.887 | 0.87963 | 0.87282 | 0.86538 | 0.85799 | 0.85116
Advanced Combustion Turbine | 1 | 1.0023 | 0.9971 | 0.99276 | 0.98589 | 0.97889 | 0.96934 | 0.95905 | 0.94727 | 0.93107 | 0.91279 | 0.8929 | 0.87977 | 0.86381 | 0.84679 | 0.83113 | 0.81871 | 0.80779 | 0.79758 | 0.78708 | 0.77806
Combined Cycle | 1 | 1.0036 | 0.99963 | 0.99655 | 0.99227 | 0.9865 | 0.97815 | 0.96905 | 0.95841 | 0.94479 | 0.93273 | 0.92275 | 0.91366 | 0.90454 | 0.89562 | 0.887 | 0.87963 | 0.87282 | 0.86538 | 0.85799 | 0.85116
Advanced Combined Cycle | 1 | 1.0028 | 0.99811 | 0.99428 | 0.98844 | 0.98194 | 0.97287 | 0.96305 | 0.95173 | 0.93656 | 0.92077 | 0.90485 | 0.89334 | 0.88011 | 0.86634 | 0.85349 | 0.8431 | 0.83382 | 0.82472 | 0.81547 | 0.80732
Adv CC w/ Sequestration | 1 | 1 | 0.99253 | 0.98592 | 0.97758 | 0.96834 | 0.95659 | 0.94415 | 0.93027 | 0.91296 | 0.89579 | 0.8792 | 0.86587 | 0.85143 | 0.83673 | 0.82277 | 0.81085 | 0.79985 | 0.78884 | 0.77777 | 0.76763
Fuel Cell | 1 | 0.98833 | 0.97678 | 0.96611 | 0.95409 | 0.94094 | 0.92515 | 0.90876 | 0.89108 | 0.87081 | 0.85219 | 0.83562 | 0.82 | 0.80447 | 0.78923 | 0.77437 | 0.7607 | 0.74759 | 0.73403 | 0.7206 | 0.70772
Nuclear | 1 | 1.001 | 0.99456 | 0.98896 | 0.95992 | 0.91168 | 0.90146 | 0.89056 | 0.8783 | 0.86335 | 0.84989 | 0.83836 | 0.82768 | 0.81701 | 0.80656 | 0.79641 | 0.78742 | 0.77895 | 0.76994 | 0.76102 | 0.75261
Biomass | 1 | 1.0022 | 0.99667 | 0.99219 | 0.98515 | 0.97816 | 0.96861 | 0.95833 | 0.94656 | 0.93186 | 0.91874 | 0.90767 | 0.89751 | 0.88734 | 0.87738 | 0.86773 | 0.85932 | 0.85147 | 0.84302 | 0.83463 | 0.8268
Landfill Gas | 1 | 1.0036 | 0.99963 | 0.99655 | 0.99227 | 0.9865 | 0.97815 | 0.96905 | 0.95841 | 0.94479 | 0.93273 | 0.92275 | 0.91366 | 0.90454 | 0.89562 | 0.887 | 0.87963 | 0.87282 | 0.86538 | 0.85799 | 0.85116
Wind (Onshore) | 1 | 1.0036 | 0.99963 | 0.99655 | 0.99227 | 0.9865 | 0.97815 | 0.96905 | 0.95841 | 0.94479 | 0.93273 | 0.92275 | 0.91366 | 0.90454 | 0.89562 | 0.887 | 0.87963 | 0.87282 | 0.86538 | 0.85799 | 0.85116
Offshore Wind | 1 | 0.99978 | 0.99202 | 0.98515 | 0.9771 | 0.96761 | 0.95561 | 0.94293 | 0.92881 | 0.91188 | 0.89654 | 0.88326 | 0.8709 | 0.85855 | 0.84646 | 0.8347 | 0.82416 | 0.81419 | 0.80366 | 0.79324 | 0.78336
Solar Thermal | 1 | 1.001 | 0.97041 | 0.96478 | 0.95799 | 0.94979 | 0.93912 | 0.92776 | 0.91497 | 0.89938 | 0.88535 | 0.87332 | 0.86219 | 0.85106 | 0.84016 | 0.82957 | 0.82019 | 0.81135 | 0.80196 | 0.79265 | 0.78388
Solar PV | 1 | 0.9047 | 0.87533 | 0.86447 | 0.8548 | 0.84537 | 0.83458 | 0.82346 | 0.81094 | 0.79596 | 0.78232 | 0.77018 | 0.75886 | 0.74717 | 0.73569 | 0.72452 | 0.7124 | 0.69766 | 0.68388 | 0.67732 | 0.67121
Dist. Gen Base | 1 | 1.001 | 0.99456 | 0.98896 | 0.98217 | 0.97392 | 0.96315 | 0.95166 | 0.9387 | 0.92287 | 0.90863 | 0.89645 | 0.88519 | 0.87392 | 0.86289 | 0.85217 | 0.8427 | 0.83378 | 0.82429 | 0.81488 | 0.80602
Dist Gen Peak | 1 | 1.001 | 0.99456 | 0.95869 | 0.90913 | 0.89817 | 0.88324 | 0.86264 | 0.84004 | 0.81646 | 0.79759 | 0.78023 | 0.76386 | 0.7497 | 0.73641 | 0.72492 | 0.71242 | 0.70417 | 0.69544 | 0.6868 | 0.67863
Source: U.S. Department of Energy, Energy Information Administration, National Energy Modeling System (NEMS). Data developed as part of Annual Energy Outlook 2017 (AEO2017).
Total Capital Cost Forecast Factors by Technology (Constant Dollar Basis)
Technology | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
Battery Energy Storage | 1 | 0.8979 | 0.80623 | 0.72391 | 0.65724 | 0.60328 | 0.55979 | 0.52502 | 0.49767 | 0.47672 | 0.46142 | 0.45122 | 0.44576 | 0.44483 | 0.44483 | 0.44483 | 0.44483 | 0.44483 | 0.44483 | 0.44483 | 0.44483
Source: Analysis by Black & Veatch

## TMO - Forecast (NEMS factors)
|  | Design Basis Parameters | [5 empty] | Technology Maturity Outlook Factor Adjusted Overnight Capital Cost (2017 Dollars)
No. | Supply-Side Option | Option Design Basis | Duty | Net Capacity (MW)(1) | Capacity Factor (%) | Primary Fuel | EIA NEMS Technology Forecast Employed | 2017 ($000) | 2018 ($000) | 2019 ($000) | 2020 ($000) | 2021 ($000) | 2022 ($000) | 2023 ($000) | 2024 ($000) | 2025 ($000) | 2026 ($000) | 2027 ($000) | 2028 ($000) | 2029 ($000) | 2030 ($000) | 2031 ($000) | 2032 ($000) | 2033 ($000) | 2034 ($000) | 2035 ($000) | 2036 ($000) | 2037 ($000)
1 | 1x0 GE 7F.05 | Combustion Turbine: GE 7F.05 Emissions Control: SCR, CO catalyst | Peaking | 231 | 11% | Natural Gas | Combustion Turbine | 143750 | 144300 | 143700 | 143300 | 142600 | 141800 | 140600 | 139300 | 137800 | 135800 | 134100 | 132600 | 131300 | 130000 | 128700 | 127500 | 126400 | 125500 | 124400 | 123300 | 122400
2 | 6x0 Wartsila 18V50SG | Recip. Engine: Wartsila 18V50SG Heat Rejection: Wet Cooling Tower Emissions Control: SCR, CO catalyst | Peaking | 110 | 25% | Natural Gas | Combustion Turbine | 145000 | 145500 | 144900 | 144500 | 143900 | 143000 | 141800 | 140500 | 139000 | 137000 | 135200 | 133800 | 132500 | 131200 | 129900 | 128600 | 127500 | 126600 | 125500 | 124400 | 123400
3 | 1x1 GE 7HA.01 | Combustion Turbine: GE 7HA.01 Duct Firing: None Emissions Control: SCR, CO catalyst Heat Rejection: Wet Cooling Tower | Intermediate | 424 | 70% | Natural Gas | Advanced Combined Cycle | 561250 | 562800 | 560200 | 558000 | 554800 | 551100 | 546000 | 540500 | 534200 | 525600 | 516800 | 507800 | 501400 | 494000 | 486200 | 479000 | 473200 | 468000 | 462900 | 457700 | 453100
4 | Biomass Combustion | Boiler: Bubbling Fluidized Bed Emissions Control: SNCR, Fabric Filter Heat Rejection: Wet Cooling Tower | Baseload | 35 | 85% | Wood | Biomass | 213500 | 214000 | 212800 | 211800 | 210300 | 208800 | 206800 | 204600 | 202100 | 199000 | 196200 | 193800 | 191600 | 189400 | 187300 | 185300 | 183500 | 181800 | 180000 | 178200 | 176500
5 | Geothermal -- Binary | System: Binary Geothermal System Heat Rejection: Air-Cooled Condenser | Baseload | 35 | 85% | n/a | Biomass | 282800 | 283400 | 281900 | 280600 | 278600 | 276600 | 273900 | 271000 | 267700 | 263500 | 259800 | 256700 | 253800 | 250900 | 248100 | 245400 | 243000 | 240800 | 238400 | 236000 | 233800
6 | Battery Storage -- Lithium Ion | Battery: Lithium Ion Discharge Duration: 2 hrs | Storage | 50 | n/a | n/a | Black & Veatch BESS Forecast | 79500 | 71400 | 64100 | 57600 | 52300 | 48000 | 44500 | 41700 | 39600 | 37900 | 36700 | 35900 | 35400 | 35400 | 35400 | 35400 | 35400 | 35400 | 35400 | 35400 | 35400
7 | Battery Storage -- Redox Flow | Battery: Redox Flow Discharge Duration: 6 hrs | Storage | 10 | n/a | n/a | Black & Veatch BESS Forecast | 41100 | 36900 | 33100 | 29800 | 27000 | 24800 | 23000 | 21600 | 20500 | 19600 | 19000 | 18500 | 18300 | 18300 | 18300 | 18300 | 18300 | 18300 | 18300 | 18300 | 18300
NOTES:
(1) Performance parameters assume ISO conditions (59 ͦ F, 60% relative humidity, and sea level elevation). Net capacity is defined as the nameplate (or gross) unit capacity, minus any auxiliary losses.
(2) Costs are provided in 2017 United States Dollars. No escalation has been applied.